## BOQ
Desirable -
Latest technology , design should be for at least the next twenty years.
Quality of treated water should be used for Flushes/ Portable.
After treatment , treated water should meet the norms set by Himachal Pradesh Pollution control Board .
The plants should be semi automated .
Capacity of STP 100 KLPD each and total plants two numbers.
BOQ FOR PROVIDING & FIXING 100 KLD STP MBBR TECHNOLOGY WITH CIVIL WORK ON TURN-KEY BASIS
Sr. No | Details of Mechanical work | Quantity | Rate | Amount
1 | S. S. Bar Screen 10mm ,SS -304 | 2 No.
2 | Sewage Feed Pumps from EQ to STP Type- Non Submersible self priming Flow rate – 5 m3/Hr | 4 Nos.
| Head – 10 meter HP/RPM- 3/2900 | (2 working +2 standby)
3 | Air Blowers for Aeration in STP and EQT Capacity – 125 m3/h | 4 Nos.
4 | Membrane Diffusers for EQ Sizes – 1 Meter | 2 Lots.
DIA - 3 Inch
5 | Membrane Diffusers for STP Sizes - 1 Meter | 2 Lots for each ZONE
DIA - 3 Inch
6 | Diffuser Lines for EQ and STP | 2 Lots.
7 | FMR/MBBR/ Media | 2 LOT
8 | Lamella/ Tube Settler modules with plates | 2 LOT
9 | Filter Feed Pumps | 4 Nos.
| Flow Rate – 8.5 m3/hr @ 25 M. Head | (2 working +2 standby)
10 | Multi Grade Filter Capacity –8.5 m3/hr | 2 No
DIA- 600 mm HOS-1875 mm
11 | Activated Carbon Filter Capacity – 8.5 m3/hr DIA-800mm | 2 No.
HOS-1875 mm
12 | Sludge Transfer Pump from SHT to Filter Press Type- Sewage Pump | 2 No.
Flow rate - 2 .5m3/hr HP/RPM- 1.5/1500
13 | Filter Press Plates- 16 Size – 14”x14” | 2 No.
14 | Agitator for Anoxic Chamber | 2 Nos.
With all accessories and mounting Arrangements
15 | Flow Meter | 4 Nos.
16 | Re-Circulation Pumps | 4 Nos.
| Cap. 7 m3/hr at 10-meter head | (2 working + 2 standby )
17 | Controller For Automation | 2 Lot.
18 | Paint work | 2Job
19 | Treated Water Storage Tank | 2 No.
20 | Treated Water Transfer Pumps | 4 Nos.
| Flow Rate – 8.5 m3/hr @ 25 M. Head | (2 working + 2 standby )
21 | Display Board for Showing the Process | 2 No.
22 | Proper MS Support for piping | 2 Set
23 | Electrical Control panel having sufficient drives, along with all pumps & | 2 Set
Motors automation and control level switches.
24 | Wiring with double tray to panel as per CPWD norms | 2 Job
25 | Wiring & cabling etc as required | 2 Job
Total Amount
GST

## CIVIL MODULAR
Details of Required Civil work - (For 100 KLD Load of Sewage )
Coloum and Beam steel 16 mm and ring 8 mm
Wall steel 12mm ( All RCC work in M25)
Sno | Description | FMR- in civil Modular | Volume of Tanks in Civil cons. | Rate | Amount
1 | Bar Screen Chamber | 1.2mX0.5mX1m | 0.6m3
2 | Oil & Grease Trap | 1.2mX.870mX2.5m | 2.61 m3
3 | Grit Chamber | 1.2mX.870mX2.5m | 2.61 m3
4 | Equalization Tank | 5 mX2.7mX2.8 m | 37.8 m3
5 | Chlorin contact cum filter feed tank | 2.2X2.5X2.3 m | 12.65m3
6 | Anoxic Tank | 1mX2.5mX4.2 m | 10.5m3
7 | Sludge Holding Tank | 1mX2.5mX2.3 m | 5.75 m3
8 | Treated Water Tank | 5 mX2.7mX2.8 m | 37.8 m3
|  | Total Volume of Tanks | m3
9 | FMR-Reactor | 6x2.5x3.5m | 52.5 m3
Total Amount
GST

## MAKE
Description | Make | MOC
Feed pump | JOHNSON/KIRLOSKAR/KSB | CI
Bar Screen | ION EXCHANGE | SS
Aeration Tank/Reactor | CIVIL TANKS | RCC
FMR Media | ION EXCHANGE | PP
Diffuser (Tube Type) | EDI, USA | Rubber (EPDM)
Blower | EVEREST/Equ. | CI
Secondary Clarifier Tank | CIVIL | RCC
Lamella Boxes and Plates | Ion Exchange | MS/FRP
Chlorination tank | CIVIL | RCC
Chlorine dosing pump | Asia LMI/ Milton ray | HDPE Tank / LDPE tank
MGF | ION EXCHANGE | MSEP
MGF Feed Pump | KIRLOSKAR / JOHNSON | CI
ACF | ION EXCHANE | MSEP
Screw Pump | UT/Roto | CI
Filter Press | Water to people/ Pharmtech
Butterfly valve | CRANE / Audco / Eqvt. | CI
Pressure gauge | H GURU / Gluke / Eqvt.
Pipe | JINDAL/TATA – B class /SUPREME | MS/PVC
Electrical panel- MCB,switch gear etc | Siemens/ L&T/ Havels/ Eqv.