## Sheet1
M/s
Address
GST
ANNEXURE A ADDRESSABLE System
Sr.No. | Description | Brand | UOM | Qty. | Rate | Value
1 | Optical Smoke Detector Supply, installation, testing and commissioning of Intelligent Addressable Optical Smoke Detector, photoelectric type, complete with built-in short circuit isolator, dual tri-colour LED indication, rotary address switches, automatic drift compensation, remote indicator output, plug-in mounting base, and complying with EN54-7 & EN54-17, suitable for operation with Notifier addressable fire alarm system | Ravel | Each | 300
2 | Multisensor smoke detector UL Approved. Dual LED’s for 360° visibility. Advanced detection and communication protocol. Polarity Insensitive. Easy installation and maintenance. Sleek low-profile housing design. Regular 100mm base. Max.254 Address setting through way DIP switch. Electrical Specification Operating Voltage 17 ~ 28V DC Reset Voltage less than 3V Standby Current 500 µA Alarm Current 7 mA. Remote Output 2mA maximum open collector Thermal Rating 59 °C (138 °F) Rate of Raise of Temp 11.1°C / min (20°F/min) Smoke Sensitivity (2.12 ± 0.61) % / ft High 1.1% ft Middle 1.4% ft Low 2.3% ft Air Velocity 0 – 4000 fpm. Operating Temperature -10 °C to 50 °C Humidity 0 – 95% RH, non-condensing | Ravel | Each | 100
3 | Heat detector Supply, installation, testing and commissioning (SITC) of Intelligent Addressable Fixed Temperature Heat Detector, 58°C (Class A1S), microprocessor-based, complete with built-in short circuit isolator, dual tri-colour LED indication, rotary address switches, automatic self-test, remote indicator output, plug-in mounting base, suitable for operation with Notifier addressable fire alarm control panel, complying with EN54-5 & EN54-17, complete in all respects. | Ravel |  | 50
4 | Manual Call Point Supply, installation, testing and commissioning (SITC) of Intelligent Addressable Manual Call Point (MCP) complete with resettable operating element/break-glass, integral red LED indication, rotary address switches, plug-in terminal block, anti-tamper locking arrangement, suitable for flush or surface mounting, complete with mounting box, test/reset key, and transparent protective cover where specified. The MCP shall be fully compatible with the Notifier addressable Fire Alarm Control Panel and shall comply with EN 54-11, complete in all respects. | Ravel | Each | 30
5 | Supply, installation, testing and commissioning (SITC) of Intelligent Addressable Electronic Hooter (Wall Sounder), loop-powered, complete with built-in short-circuit isolator, minimum sound output of 95 dB(A) at 1 metre, 32 selectable tones, 3 selectable volume levels, rotary address switches, tamper-resistant enclosure, suitable for operation with the Notifier addressable Fire Alarm Control Panel, complying with EN 54-3, complete with mounting accessories and all necessary hardware. | Ravel | Each | 30
6 | Supply, installation, testing and commissioning (SITC) of 4-Loop Intelligent Addressable Fire Alarm Control Panel, microprocessor-based, modular construction, complete with backlit LCD display, minimum 159 detectors and 159 modules per loop, FlashScan communication protocol, programmable logic, event history, automatic drift compensation, battery charger, power supply, network communication capability, alarm/trouble/supervisory relays, suitable for operation with Notifier addressable detectors, modules, manual call points and notification appliances. The panel shall be complete with batteries, enclosure, all necessary accessories, and shall comply with applicable UL 864/NFPA 72 requirements, suitable for ESSAR refinery and industrial fire detection systems | Ravel | Each | 1
7 | Supply, installation, testing and commissioning (SITC) of Intelligent Remote LCD Repeater Panel (Remote Annunciator) complete with 640-character backlit LCD display, LED indications for Alarm, Trouble, Supervisory and Power, alarm acknowledge, silence and reset functions, password-protected operation, RDP/RS-485 communication interface, lockable wall-mounted enclosure, complete with power supply interface, communication wiring accessories and all necessary hardware. The repeater panel shall be fully compatible with the Notifier ONYX Series Fire Alarm Control Panel and shall comply with UL 864 and NFPA 72, suitable for ESSAR refinery and industrial fire alarm applications | Ravel |  | 1
8 | Supply, laying, testing and commissioning of 2 Core × 1.5 sq.mm Copper Armoured FRLS Cable, 1100 V grade, stranded Class-2 plain annealed copper conductor, XLPE insulated, PVC inner sheathed, galvanized steel wire armoured, FRLS PVC outer sheathed (red colour), conforming to IS 7098 (Part 1), IS 8130 and IS 5831, complete with all accessories including glands, lugs, ferrules, clamps, identification tags, testing, termination and commissioning, as required. | Polycab | mtr | 8000
9 | Supply and installation of Heavy Duty Mild Steel (MS) Conduit, BEC make or approved equivalent, manufactured from ERW steel tube conforming to IS 9537 (Part 2), threaded at both ends complete with coupler, bends, junction boxes, inspection boxes, saddles, locknuts, brass bushes, accessories, supports, clamps, cutting, threading, fixing, testing and commissioning, complete in all respects. | BEC | mtr | 3000
10 | Supply, installation, testing and commissioning (SITC) of Intelligent Addressable Control Module, Notifier FCM-1 or approved equivalent, complete with rotary address switches, panel-controlled LED indication, supervised Class A/Class B output circuit, suitable for switching externally powered 24 VDC notification appliances and fire protection equipment, compatible with FlashScan protocol, mountable in a standard 4-inch electrical box, complete with end-of-line device, wiring accessories, testing and commissioning, complying with UL 864 and suitable for ESSAR refinery and industrial fire alarm systems | Ravel | Each | 30
11 | Supply, installation, testing and commissioning (SITC) of Intelligent Addressable Monitor Module, Notifier FMM-1 or approved equivalent, complete with rotary address switches, panel-controlled LED indication, supervised Class A/Class B initiating device circuit, 47 kΩ end-of-line resistor, mounting hardware, and all accessories. The module shall be loop-powered, compatible with Notifier FlashScan intelligent fire alarm control panels, suitable for monitoring dry-contact devices such as water flow switches, valve supervisory switches, pressure switches, and conventional manual call points, complying with UL 864 and suitable for ESSAR refinery and industrial fire alarm systems | Ravel | Each | 1
12 | Supply, installation, testing and commissioning (SITC) of Intelligent Fault Isolator Module, Notifier ISO-X(A) or approved equivalent, loop-powered, suitable for automatic isolation of wire-to-wire short circuits on the Signaling Line Circuit (SLC), complete with LED status indication, automatic reset after fault clearance, mounting hardware, and all accessories. The module shall support Style 4, Style 6 and Style 7 wiring, mount in a standard 4-inch junction box, and be fully compatible with Notifier ONYX/FlashScan addressable fire alarm control panels. The module shall comply with UL 864 and be suitable for ESSAR refinery, petrochemical, and industrial fire alarm applications | Ravel | Each | 10
13 | Supply of Beam Detector consisting of 4 wire systems with Infrared emitter receiver in a single housing and Four reflector plates 5-100mtrs. Range - equipped with built-in automatic compensation - inbuilt laser light for easy alignment - Option for remote indication -Three sensitivity threshold of 18%, 30% & 50% -Zone Interface Module :Module Status by RED LED.Analogue Communication with the panel. Module Addressing by 8 way DIP Switches. Low Standby Current. Operating Voltage 24VDC Current Draw(SLC) 0.5mA, (2 mA Max.Latched) External Supply Voltage Regulated 24VDC External Supply Standby Current 5mA External Supply Alarm Current 60mA Max. Communication Line loop impedance 40 Ohm End Of Line Resistor 4.7K Ohms. Temperature Range 0°C to 49°C / 32°- 120°F Humidity 93 ± 2% RH (non-condensing) at 32 ±2° C / 90 ±3° F . No. Parameters Value 1. Max. Sound pressure level 120 dB 2. Frequency response 400-12000 Hz 3. Power supply PoE+(IEEE 802.3at) 4. Housing Impact resistant Aluminum 5. Ingress Protection IP 65 6. Mounting Indoor 7. Reliability Designed for 24/7 operations 8. Network protocols IPv4/v6, HTTP, HTTPS, SIP, | Ravel | Each | 4
| Total-A |  |  |  |  | 0
FIRE AUTOMATIC HYDRANT SYSTEM-B
1 | Providing, fixing, testing and commissioning of above ground M S ERW Black Heavy duty pipes class C as per IS:1239 and IS:3589 including cutting, screwing, welding etc. and providing all fittings like, elbows, reducers,etc. | Tata/Jindal
| 80 mm dia. |  | RM | 1568
| 25 mm dia. |  | RM | 60
4 | Providing, fixing, testing and commissioning of SS single headed ISI marked oblique pattern hydrant landing valves as per IS: 5290 with 80 mm dia flanged inlet & 63 mm dia female outlet complete with PVC cap. | Alfa/Saviour | Nos | 15
5 | Providing, fixing, testing and commissioning of 63 mm dia 15m long RRL hose pipe (CRC MAKE) with 63 mm dia. Male and female SS couplings duly binded with SS wire, rivets etc. conforming to IS 636 (type-B) as required. | Alfa/Saviour | Each | 30
6 | Providing, fixing, testing & commissioning of Standard SS branch pipe with nozzle of 20mm nominal bore outlet as per IS:903 suitable to fit with standard instanteneous type 63mm dia coupling. | Alfa/Saviour | Each | 15
7 | Providing, fixing, testing & commissioning of Wall mounting swing type first aid Fire Hose Reel with drum, hanging bracket, 30 M x 20 mm dia high pressure hose reel tubing as per IS:444 with gun metal shut of nozzle all required accessories. | Alfa/Saviour | Each | 15
8 | Providing, fixing, testing and commissioning of Weather proof standard fire hose cabinet wall mounting type (750 mm x 600 mm x 250 mm deep) having single or double opening with necessary locking arrangement by allan key suitable for housing 2 nos. hose pipe, 1no. Branch pipe & nozzle spaner. | Alfa/Saviour | Each | 15
9 | Providing, fixing, testing and commissioning of standard fire hose case wall mounting type single or double opening with necessary locking arrangement | Fabricated | Each | 15
10 | Supplying, fixing, testing and commissioning of GUN METAL Four way fire brigade inlet as per IS:904 having 63 mm dia inlet with blank cap and chain with necessary fittings, flanges, nutbolts etc. | Alfa/Saviour | Each | 0
11 | Foam monitor Monitors are fixed fire suppression discharge devices used in the application of firefighting water or foam solution to a specific area or risk. Monitors are an effective way of covering large areas of application. | Alfa/Saviour | Each | 6
| Total B |  |  |  |  | 0
| Grand Total (A+B) |  |  |  |  | 0
Scope:
1 | Supply, Installation, Testing and Commissioning
2 | Delivery till Project site (Inclusive of Freight)
3 | Internal Electrical cables and Trays Supply and laying as per BOQ
4 | Unloading, Internal movement of material at site, To & Fro Travel charges,
5 | Scaffolding, Crane / Hydra, IN CLIENT SCOPE. Painting (as referred in the BOQ).
6 | Testing of the Entire fire Hydrant system line as per requirement
7 | Makes, MOCs as per BOQ shall be followed.
8 | Mobilization time max- 10 Days from the date of confirmed PO
9 | Pipe Quantity may vary as per site condition
10 | Earthing Strip in vendor scope
11 | Civil work in vendor scope
12 | Drawings and good for construction drawings in vendor scope
13 | Also submit a Bank Draft of Rs. 50,000/- as EMD amount alongwith Tender.
14 | Vendor must visit the site before submitting the proposal to understand the scope of work.