## Summary
LSS_Summary for Bill of Quantities_ Refurbishment of Hospital
Sr. No | Head | Amount
1 | Refurbishment of Main Building | 0
2 | Refurbishment of Tin Huts | 0
| Total | 0
| Grand Total | 0

## Abstract For Tin Hut
LSS_Bill of Quantities_Refurbishment of Hospital-Tin Hut_07.05.2026
Sr. No. | Item Description | Unit | Quantity | Rate | Amount | Reference
A.Dismantling & Demolishing
A1 | Dismantling of flexible pavement (bituminous courses) by mechanical means and disposal of dismantled material up to a lead of 1 kilometre, as per direction of Engineer-in-charge. | cum | 8 |  | 0
A2 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | cum | 37.5008 |  | 0
A3 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead. For thickness of tiles 10 mm to 25 mm | sqm | 169.9968 |  | 0
A4 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | cum | 2 |  | 0
A5 | Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of: G.S. Sheet | sqm | 300 |  | 0
A6 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar | cum | 3.9954 |  | 0
A7 | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead. | Each | 9 |  | 0
A8 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. | sqm | 379.9992 |  | 0
A9 | Careful removal of existing wooden false ceiling, including all supporting framework, battens, and fixtures, ensuring minimum damage to adjoining surfaces; stacking of all serviceable material at designated location within site premises as directed by the Engineer-in-Charge. | L.S
| Total A |  |  |  | 0
B. Masonry and Flooring & Wood Work
B1 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including getting out and disposal of excavated earth upto 50 m and lift upto 1.5 m, as directed by Engineer-in- Charge: All kinds of soil | sqm | 350 |  | 0
B2 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75 mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth. | sqm | 200.0019 |  | 0
B3 | 40 mm thick fine dressed stone flooring over 20 mm (average) thick base of cement mortar 1:5 (1 cement : 5 coarse sand) with joints finished flush. White sand stone | sqm | 200.0019 |  | 0
B4 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | cum | 37.5001 |  | 0
B5 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement mortar 1:4 (1 cement : 4 coarse sand) | cum | 15.0003 |  | 0
B6 | 12 mm cement plaster finished with a floating coat of neat cement of mix : 1:4 (1 cement: 4 fine sand) | sqm | 224.9996 |  | 0
B7 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. Two coats | sqm | 300 |  | 0
B8 | Providing and fixing approved quality natural stone cladding of 18–25 mm thickness, in required sizes, shapes, and patterns, on walls, columns, or façade surfaces, as per drawings, specifications, and as directed by the Engineer-in-Charge. | sqm | 110 |  | 0
B9 | Structural steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. Heavy weight grating made with equal leg angle frame of 40x40x5 and Shutter of 35x35x5 ms angle with Ms flat (30x5)mm at top . the spacing between ms flat is 50mm dimensions, total weight of cover and frame to be not less than 30 kg | kg | 3700 |  | 0
B10 | Providing and laying 4" x 4" Polycrete pavers of dark gray and medium gray shades (as per sample approved) over a prepared base in cement mortar 1:4 (1 part cement : 4 parts coarse sand), including preparation of base, leveling, laying in approved pattern, filling of joints with fine sand/cement slurry, compacting, and curing, complete as per drawing and direction of the Engineer-in-Charge. | sqm | 70.0027 |  | 0
B11 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished seamless type tubes | kg | 199.9984 |  | 0
B12 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : 25 mm thick | sqm | 199.9976 |  | 0
B13 | Kota stone slabs 20 mm thick in risers of steps, skirting, dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement: 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slabs, including rubbing and polishing complete. | sqm | 25.0001 |  | 0
B14 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm(thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), Jointing with grey cement slurry @ 3.3 kg/sqm including pointing the joints with white cement and matching pigment etc., complete. | sqm | 149.9958 |  | 0
B15 | Providing & Fixing double skin full height 12 mm thick solid partition of make STYLAM or similar (upto the 7 feet), vertical members to be fixed on the SS plate and caping on the floor. Approved BWR ply as per IS:303, finished both side with approved 1 mm laminate surface complete with door shutter with laminate finish matching to the other available side of the partition, to be incorporated with necessary hinges, sliding bolt from inside, handle and all complete as per design, direction and approval of the Engineer. | sqm | 30 |  | 0
B16 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length (hold fast lugs or dash fastener shall be paid for separately). Sal wood | cum | 0.5 |  | 0
B17 | Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows, fixing with butt hinges of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. (Note: Butt hinges and necessary screws shall be paid separately) Second class teak wood | sqm | 30 |  | 0
B18 | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick. |  |  |  | 0
a | Second class teak wood | sqm | 20 |  | 0
b | Float glass panes-4 mm thick glass pane (weight not less than 10 kg/sqm). | sqm | 10 |  | 0
B18 | Careful repair and refurbishment of existing wooden doors and windows, including minor dismantling, replacement of decayed wood with matching timber, tightening of joints, surface preparation, anti-termite treatment, repair/refixing of fittings, and replacement of broken or damaged glass panes where required, complete with polishing/painting as per engineer in charge. | L.S
| Total B |  |  |  | 0
C. Roofing works
C1 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer onboth side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | sqm | 350 |  | 0
C2 | Providing and fixing precoated galvanised steel sheet roofing accessories of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05 mm) with Zinc coating 120 gram per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete :
C2.1 | Flashings/ Aprons.( Upto 600 mm) | metre | 240 |  | 0
C2.2 | Gutter (600 mm over all girth) | metre | 100 |  | 0
C3 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | kg | 523.764 |  | 0
| Total C |  |  |  | 0
D. Plumbing & Sanitary works
D1 | Providing and fixing white vitreous china extended wall mounting water closet of size 780x370x690 mm of approved shape including providing & fixing white vitreous china cistern with dual flush fitting, of flushing capacity 3 litre/ 6 litre (adjustable to 4 litre/ 8 litres), including seat cover, and cistern fittings, nuts, bolts and gasket etc complete. | Each | 7 |  | 0
D2 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require: White Vitreous China Flat back wash basin size 450x 300 mm with single 15 mm C.P. brass pillar tap | Each | 5 |  | 0
D3 | Providing and fixing CP Brass 32 mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge. | Each | 5 |  | 0
D4 | Providing and fixing toilet paper holder : C.P. brass | Each | 7 |  | 0
D5 | Providing and fixing Health faucet with 1 metre long Flexible tube and C.P. wall hook with PVC & SS Screws wherever required make and as per the direction of Engineer-in-charge. | Each | 7 |  | 0
D6 | Providing and fixing of C.P. Soap dish complete as per instruction of Engineer-in-charge. | Each | 5 |  | 0
D7 | Providing and fixing C.P Towel Rail 600mm long fixed to PVC cleats with C.p brass screws including cutting and making good the walls wherever required. | Each | 4 |  | 0
D8 | Providing and fixing C.P Single lever concealed diverter and Bath spout for bath and shower with Button at Top complete as per direction of the Engineer-in-charge | Each | 3 |  | 0
D9 | Providing and Fixing Shower Head Over head rose shower with revoling joint ( with boday roation) & 115 mm long shower arm complete as directed by enginner in charge | Each | 2 |  | 0
D10 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore | Each | 7 |  | 0
D11 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. 15 mm nominal bore | Each | 10 |  | 0
D12 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 15 mm nominal bore | Each | 10 |  | 0
D13 | Providing and fixing of C.P towel ring square/circular fixed to wooden cleats with C.P brass screws including cutting and making good the walls wherever required. | Each | 4 |  | 0
D14 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings and fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc.
| 15 mm nominal dia Pipes | metre | 100 |  | 0
| 20 mm nominal dia Pipes | metre | 80 |  | 0
| 25 mm nominal dia Pipes | metre | 80 |  | 0
| 32 mm nominal dia Pipes | metre | 70 |  | 0
D15 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work
| 15 mm nominal dia Pipes | metre | 150 |  | 0
| 20 mm nominal dia Pipes | metre | 120 |  | 0
| 25 mm nominal dia Pipes | metre | 60 |  | 0
| 32 mm nominal dia Pipes | metre | 50 |  | 0
D16 | Providing and laying Non Pressure NP-3 class (Medium duty) R.C.C. pipes including collars/spigot jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of jointsetc. Complete 450 mm dia RCC pipes. | rmt | 20 |  | 0
D17 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | each | 2 |  | 0
| Total D |  |  |  | 0
E.Electrical Work
Point Wiring: Point wiring rates are inclusive of 2X2.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit and 1.5 sq mm FRLS PVC insulated copper conductor insulated earth wire.
E1 | Supply, Wiring, Testing & Commissioning for switch board controlled light points with 3 X 1.5sq.mm FRLS PVC insulated copper wire and earthing with 1.5 sq.mm. FRLS PVC insulated copper wire in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of modular switches as specified complete with modular plate with GI boxes of suitable as complete as required.
E1.1 | First Point (One point controlled by one no. 6 amps switch.) (Normal Light Point) | Nos | 39 |  | 0
E1.2 | same as the above for Looping Point | Nos | 13 |  | 0
E2 | Supply, Wiring, Testing & Commissioning for MCB controlled light points with 2 x 2.5 + 1 X 1.5 sq.mm FRLS PVC insulated copper wires in recessed / surface mounted in in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles, conduit fixing material, MS Connector, along with all required fittings. (Cost of MCB not to be included)
E2.1 | First Point (First light points controlled by one no.6A SP MCB) | Nos | 11 |  | 0
E2.2 | same as above for the Looping Point | Nos | 5 |  | 0
E3 | Supply, Wiring, Testing & Commissioning for 6 A multistandard shutterd switched socket outlet with 3 x 1.5 sq mm FRLS PVC insulated copper wire & earthing with 1.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of 6amps modular switch, socket complete with modular plate with suitable size of GI box complete in all respect. | Nos | 28 |  | 0
E4 | Supply, Wiring, Testing & Commissioning for 1 nos, 16 A shuttered, switched socket outlets with 2 x4 +1 x 2.5 sq.mm FRLS PVC insulated copper wire & earthing with 2.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, including providing & fixing of 1 nos. of 16amps modular switched socket outlets alongwith 1nos 16 A switch with modular plate with GI box complete. | Pt. | 16 |  | 0
E5 | Supply and wiring of exhaust fan point with 3 X 1.5 sq.mm FRLS PVC insulated copper conductor cable in in surface / recessed GI conduit, fixing on surface or wall/ceiling including fixing of saddles etc. including galvanised M.S. box, modular range of plate switches, 6A socket, modular cover plate, PVC insulated copper earth wire etc. complete as required. | Nos | 7 |  | 0
E6 | Wiring for the Ceiling fan points with 3X1.5 Sq.mm PVC insulated stranded copper conductor wires in concealed FRLS PVC. conduits in ceiling / walls as directed including providing Hexagonal fan Box , Electronic fan regulator,6 amp switch, 5 sided G.I. Boxes for housing the regulator and earthing complete as required. | Nos | 7 |  | 0
E7 | Providing and fixing in position the following FRLS PVC conduits including all accessories concealed in F. ceiling (PVC conduit not to be instaUed above false ceilfng) /waif/ floor as required including M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl-ete with 1.6 mm dia G.I. pull wires in the length of conduit.
E7.1 | 20 mm dia conduit ( 1.6 mm thick) | rmt | 50 |  | 0
E7.2 | 25 mm dia conduit (1.6 mm thick) | rmt | 60 |  | 0
E7.3 | 32 mm dia conduit (2.0 mm thick) | rmt | 40 |  | 0
E8 | Supply,installing ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm-in proof, with hinged and lockable doors complete with DP MCB's and inter- connection with copper wire , insulated copper bus bar , cable glands-/conduit entry bushes, bonding to earth and paint-ing. Also provide separate neutral: busbar for each phase. Provide separate ,Earth Links for each phase. Use brass thimbles for connections of all: wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated.
E8.1 | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB. | nos | 3 |  | 0
E8.2 | 8 Way TPN DB, each phase consisting of 6 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB. | nos | 2 |  | 0
E8.3 | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB. | nos | 2 |  | 0
E9 | Supply, Installation, Testing & Commissioning of 1200 mm dia 5 Star rated ceiling fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ). | Each | 7 |  | 0
E10 | Supply & Installation, Testing & Commissioning of 250 mm dia exhaust fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ). | Each | 18 |  | 0
E11 | Supplying of light fixtures as per sample approved. | L.S
| Total E |  |  |  | 0
| Total (A+B+C+D+E) |  |  |  | 0
| Grand Total |  |  |  | 0

## Measurement Sheet For Tin Hut
LSS_Takeoff Sheet_Refurbishment of Hospital-Tin Hut_07.05.2026
S.N0 | Item Description | Nos | L | W | H/D | Qty. | Unit
A.Dismantling & Demolishing
A1 | Dismantling of flexible pavement (bituminous courses) by mechanical means and disposal of dismantled material up to a lead of 1 kilometre, as per direction of Engineer-in-charge.
Outside area as per drawing - 58 sqm
| Taking 100 mm depth |  |  |  |  | 5.8 | cum
| At different location as per structure demand |  |  |  |  | 2.2 | cum
| Total |  |  |  |  | 8 | cum
A2 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.
In Isolation Ward 1
| Main ward |  | 13.7 | 3 | 0.1 | 4.11 | cum
| Room 1 |  | 3.7 | 2.6 | 0.1 | 0.962 | cum
| Toilet |  | 2.9 | 3 | 0.1 | 0.87 | cum
| Toilet 1 |  | 1.8 | 1.8 | 0.1 | 0.324 | cum
In Isolation Ward 2
| Main ward |  | 10.41 | 4.98 | 0.1 | 51.8418 | cum
| Room 1 |  | 3.14 | 4.98 | 0.1 | 15.6372 | cum
| Room 2 |  | 1.8 | 2 | 0.1 | 3.6 | cum
Toilet
| Toilet 1 |  | 2.12 | 2.46 | 0.1 | 5.2152 | cum
| Toilet 2 |  | 3.46 | 2.81 | 0.1 | 9.7226 | cum
Outside area as per drawing
| 1 |  |  |  |  | 15.315 | cum
| 2 |  |  |  |  | 10.855 | cum
| At different location as per structure demand |  |  |  |  | 6.55 | sqm
| Total |  |  |  |  | 125.0028 | cum
| taking 30% quantity |  |  |  |  | 37.5008 | cum
A3 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead. For thickness of tiles 10 mm to 25 mm
In Isolation Ward 1
| Main ward |  | 13.7 | 3 |  | 41.1 | sqm
| Room 1 |  | 3.7 | 2.6 |  | 9.62 | sqm
| Toilet |  | 2.9 | 3 |  | 8.7 | sqm
| Toilet 1 |  | 1.8 | 1.8 |  | 3.24 | sqm
In Isolation Ward 2
| Main ward |  | 10.41 | 4.98 |  | 51.8418 | sqm
| Room 1 |  | 3.14 | 4.98 |  | 15.6372 | sqm
| Room 2 |  | 1.8 | 2 |  | 3.6 | sqm
Toilet
| Toilet 1 |  | 2.12 | 2.46 |  | 5.2152 | sqm
| Toilet 2 |  | 3.46 | 2.81 |  | 9.7226 | sqm
| At different location as per structure demand |  |  |  |  | 21.32 | sqm
| Total |  |  |  |  | 169.9968 | sqm
A4 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge.
| At different location as per structure demand |  |  |  |  | 2 | cum
A5 | Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of: G.S. Sheet
| For Isolation Ward 1 |  |  |  |  | 125 | sqm
| For Isolation Ward 2 |  |  |  |  | 135 | sqm
| At different location as per structure demand |  |  |  |  | 40 | sqm
| Total |  |  |  |  | 300 | sqm
A6 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar
In Isolation Ward 1
|  | 2 | 1.2 | 0.14 | 1.62 | 0.54432 | cum
In Isolation Ward 2
|  | 1 | 1.2 | 0.14 | 1.56 | 0.26208 | cum
|  | 2 | 1.2 | 0.18 | 1.56 | 0.67392 | cum
|  | 2 | 1.11 | 0.13 | 1.56 | 0.45022 | cum
|  | 2 | 1.22 | 0.13 | 1.56 | 0.49483 | cum
| At different location as per structure demand |  |  |  |  | 1.57 | cum
| Total |  |  |  |  | 3.9954 | cum
A7 | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead.
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Toilet | 6 |  |  |  | 6 | nos
nos
| Total |  |  |  |  | 9 | nos
A8 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead.
In Isolation Ward 1
Main ward
| Wall 1 |  | 13.7 | 2.42 |  | 33.154 | sqm
| Wall 2 |  | 3 | 2.79 |  | 8.37 | sqm
| Wall 3 |  | 13.7 | 2.36 |  | 32.332 | sqm
| Wall 4 |  | 3 | 2.79 |  | 8.37 | sqm
Room 1
| Wall 1 |  | 3.7 | 2.28 |  | 8.436 | sqm
| Wall 2 |  | 2.6 | 2.79 |  | 7.254 | sqm
| Wall 3 |  | 3.7 | 2.56 |  | 9.472 | sqm
| Wall 4 |  | 2.6 | 2.79 |  | 7.254 | sqm
Toilet
| Wall 1 |  | 2.9 | 2.42 |  | 7.018 | sqm
| Wall 2 |  | 3 | 2.79 |  | 8.37 | sqm
| Wall 3 |  | 2.9 | 2.36 |  | 6.844 | sqm
| Wall 4 |  | 3 | 2.79 |  | 8.37 | sqm
Toilet 1
| Wall 1 |  | 1.8 | 2.83 |  | 5.094 | sqm
| Wall 2 |  | 1.8 | 2.83 |  | 5.094 | sqm
| Wall 3 |  | 1.8 | 2.52 |  | 4.536 | sqm
| Wall 4 |  | 1.8 | 2.83 |  | 5.094 | sqm
In Isolation Ward 2
Main ward
| Wall 1 |  | 10.41 | 3.21 |  | 33.4161 | sqm
| Wall 2 |  | 4.98 | 3.67 |  | 18.2766 | sqm
| Wall 3 |  | 10.41 | 3.21 |  | 33.4161 | sqm
| Wall 4 |  | 4.98 | 3.67 |  | 18.2766 | sqm
Room 1
| Wall 1 |  | 3.14 | 3.21 |  | 10.0794 | sqm
| Wall 2 |  | 4.97 | 3.67 |  | 18.2399 | sqm
| Wall 3 |  | 3.14 | 3.21 |  | 10.0794 | sqm
| Wall 4 |  | 4.97 | 3.67 |  | 18.2399 | sqm
Room 2
| Wall 1 |  | 1.8 | 2.42 |  | 4.356 | sqm
| Wall 2 |  | 2 | 2.4 |  | 4.8 | sqm
| Wall 3 |  | 1.8 | 2.42 |  | 4.356 | sqm
| Wall 4 |  | 2 | 1.96 |  | 3.92 | sqm
Toilet
| Wall 1 |  | 2.12 | 3.18 |  | 6.7416 | sqm
| Wall 2 |  | 2.45 | 3.09 |  | 7.5705 | sqm
| Wall 3 |  | 1.34 | 3 |  | 4.02 | sqm
| Wall 4 |  | 2.81 | 2.93 |  | 8.2333 | sqm
| Wall 5 |  | 3.46 | 3.18 |  | 11.0028 | sqm
| Wall 6 |  | 5.28 | 3.32 |  | 17.5296 | sqm
| Total a |  |  |  |  | 397.6158 | sqm
Deduction
In Isolation Ward 1
| Door 1 | 2 | 1.37 | 2.02 |  | 5.5348 | sqm
| Door 2 | 1 | 0.89 | 1.84 |  | 1.6376 | sqm
| Door 3 | 1 | 0.69 | 2.04 |  | 1.4076 | sqm
| Door 4 | 1 | 0.66 | 2.04 |  | 1.3464 | sqm
| Window 1 | 4 | 0.86 | 1 |  | 3.44 | sqm
| Window 2 | 1 | 0.66 | 0.8 |  | 0.528 | sqm
| Ventilator 1 | 1 | 0.56 | 0.43 |  | 0.2408 | sqm
| Ventilator 2 | 2 | 0.57 | 0.53 |  | 0.6042 | sqm
In Isolation Ward 2
| Door 1 | 2 | 1.37 | 2.31 |  | 6.3294 | sqm
| Door 2 | 2 | 0.66 | 2.18 |  | 2.8776 | sqm
| Window 1 | 3 | 1.11 | 1.4 |  | 4.662 | sqm
| Window 2 | 3 | 0.56 | 1.34 |  | 2.2512 | sqm
| Ventilator 1 | 1 | 0.87 | 0.6 |  | 0.522 | sqm
| Ventilator 2 | 1 | 0.63 | 0.38 |  | 0.2394 | sqm
| Ventilator 3 | 4 | 0.73 | 0.43 |  | 1.2556 | sqm
| Total b |  |  |  |  | 32.8766 | sqm
| Total (a-b) |  |  |  |  | 364.7392 | sqm
| At different location as per structure demand |  |  |  |  | 15.26 | sqm
| Total |  |  |  |  | 379.9992 | sqm
A9 | Careful removal of existing wooden false ceiling, including all supporting framework, battens, and fixtures, ensuring minimum damage to adjoining surfaces; stacking of all serviceable material at designated location within site premises as directed by the Engineer-in-Charge.
| At different location as per structure demand |  |  |  |  | 1 | Job
B. Masonry and Flooring & Wood Work
B1 | Earth work in surface excavation not exceeding 30 cm in depth but exceeding 1.5 m in width as well as 10 sqm on plan including getting out and disposal of excavated earth upto 50 m and lift upto 1.5 m, as directed by Engineer-in- Charge: All kinds of soil
| Outside area as per drawing |  |  |  |  | 284.7 | sqm
| At different location as per structure demand |  |  |  |  | 65.3 | sqm
| Total |  |  |  |  | 350 | sqm
B2 | Making plinth protection 50 mm thick of cement concrete 1:3:6 (1 cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) over 75 mm thick bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including necessary excavation, levelling & dressing & finishing the top smooth.
Isolation Ward 1
| Location 1 |  | 4.94 | 0.6 |  | 2.964 | sqm
| Location 2 |  | 2.35 | 1.95 |  | 4.5825 | sqm
| Location 3 |  | 24.02 | 0.6 |  | 14.412 | sqm
| Location 4 |  | 6.98 | 0.6 |  | 4.188 | sqm
Isolation Ward 2
| Location 1 |  | 19.44 | 0.6 |  | 11.664 | sqm
| Location 2 |  | 4.77 | 0.6 |  | 2.862 | sqm
| Location 3 |  | 1.94 | 2.46 |  | 4.7724 | sqm
| Location 4 |  | 20.86 | 1.64 |  | 34.2104 | sqm
Hardscape
| Location 1 |  | 19.53 | 3 |  | 58.59 | sqm
| Location 2 |  | 7.02 | 2.48 |  | 17.4096 | sqm
| Location 3 |  | 1.65 | 1.66 |  | 2.739 | sqm
| Location 4 |  | 24.03 | 1.4 |  | 33.642 | sqm
| At different location as per structure demand |  |  |  |  | 10.93 | sqm
| Total |  |  |  |  | 200.0019 | sqm
B3 | 40 mm thick fine dressed stone flooring over 20 mm (average) thick base of cement mortar 1:5 (1 cement : 5 coarse sand) with joints finished flush. White sand stone
Isolation Ward 1
| Location 1 |  | 4.94 | 0.6 |  | 2.964 | sqm
| Location 2 |  | 2.35 | 1.95 |  | 4.5825 | sqm
| Location 3 |  | 24.02 | 0.6 |  | 14.412 | sqm
| Location 4 |  | 6.98 | 0.6 |  | 4.188 | sqm
Isolation Ward 2
| Location 1 |  | 19.44 | 0.6 |  | 11.664 | sqm
| Location 2 |  | 4.77 | 0.6 |  | 2.862 | sqm
| Location 3 |  | 1.94 | 2.46 |  | 4.7724 | sqm
| Location 4 |  | 20.86 | 1.64 |  | 34.2104 | sqm
Hardscape
| Location 1 |  | 19.53 | 3 |  | 58.59 | sqm
| Location 2 |  | 7.02 | 2.48 |  | 17.4096 | sqm
| Location 3 |  | 1.65 | 1.66 |  | 2.739 | sqm
| Location 4 |  | 24.03 | 1.4 |  | 33.642 | sqm
| At different location as per structure demand |  |  |  |  | 10.93 | sqm
| Total |  |  |  |  | 200.0019 | sqm
B4 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources)
For drain
| 1) |  | 12.77 | 0.965 | 0.1 | 1.2323 | cum
| 2) |  | 19.44 | 0.965 | 0.1 | 1.876 | cum
| 3) |  | 6.98 | 0.965 | 0.1 | 0.67357 | cum
| 4) |  | 24.06 | 0.965 | 0.1 | 2.3218 | cum
| 5) |  | 6.55 | 0.965 | 0.1 | 0.63207 | cum
| 6) |  | 21.36 | 0.965 | 0.1 | 2.0612 | cum
| 7) |  | 2.81 | 0.965 | 0.1 | 0.27117 | cum
| 8) |  | 10.32 | 0.965 | 0.1 | 0.99588 | cum
| 9) |  | 12.73 | 0.965 | 0.1 | 1.2284 | cum
In Isolation Ward 1
| Main ward |  | 13.7 | 3 | 0.1 | 4.11 | cum
| Room 1 |  | 3.7 | 2.6 | 0.1 | 0.962 | cum
| Toilet |  | 2.9 | 3 | 0.1 | 0.87 | cum
| Toilet 1 |  | 1.8 | 1.8 | 0.1 | 0.324 | cum
In Isolation Ward 2
| Main ward |  | 10.41 | 4.98 | 0.1 | 51.8418 | cum
| Room 1 |  | 3.14 | 4.98 | 0.1 | 15.6372 | cum
| Room 2 |  | 1.8 | 2 | 0.1 | 3.6 | cum
Toilet
| Toilet 1 |  | 2.12 | 2.46 | 0.1 | 5.2152 | cum
| Toilet 2 |  | 3.46 | 2.81 | 0.1 | 9.7226 | cum
Stone
| 1) |  | 1.85 | 6.53 | 0.1 | 1.2081 | cum
| 2) |  | 2.05 | 2.75 | 0.1 | 0.56375 | cum
| 3) |  | 6.24 | 5.48 | 0.1 | 0.56375 | cum
| 4) |  | 1.95 | 2.81 | 0.1 | 3.4195 | cum
| At different location as per structure demand |  |  |  |  | 15.67 | cum
| Total |  |  |  |  | 125.0003 | cum
| taking 30% quantity |  |  |  |  | 37.5001 | cum
B5 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement mortar 1:4 (1 cement : 4 coarse sand)
Brick work for drain
| 1) | 2 | 12.77 | 0.23 | 0.3 | 1.7623 | cum
| 2) | 2 | 19.44 | 0.23 | 0.3 | 2.6827 | cum
| 3) | 2 | 6.98 | 0.23 | 0.3 | 0.96324 | cum
| 4) | 2 | 24.06 | 0.23 | 0.3 | 3.3203 | cum
| 5) | 2 | 6.55 | 0.23 | 0.3 | 0.9039 | cum
| 6) | 2 | 21.36 | 0.23 | 0.3 | 2.9477 | cum
| 7) | 2 | 2.81 | 0.23 | 0.3 | 0.38778 | cum
| 8) | 2 | 10.32 | 0.23 | 0.3 | 1.4242 | cum
| 9) | 2 | 12.73 | 0.23 | 0.3 | 1.7567 | cum
| At different location as per structure demand |  |  |  |  | 7.58 | cum
| Total |  |  |  |  | 15.0003 | cum
B6 | 12 mm cement plaster finished with a floating coat of neat cement of mix : 1:4 (1 cement: 4 fine sand)
In Isolation Ward 1
Main ward
| Wall 1 |  | 13.7 | 2.42 |  | 33.154 | sqm
| Wall 2 |  | 3 | 2.79 |  | 8.37 | sqm
| Wall 3 |  | 13.7 | 2.36 |  | 32.332 | sqm
| Wall 4 |  | 3 | 2.79 |  | 8.37 | sqm
Room 1
| Wall 1 |  | 3.7 | 2.28 |  | 8.436 | sqm
| Wall 2 |  | 2.6 | 2.79 |  | 7.254 | sqm
| Wall 3 |  | 3.7 | 2.56 |  | 9.472 | sqm
| Wall 4 |  | 2.6 | 2.79 |  | 7.254 | sqm
Toilet
| Wall 1 |  | 2.9 | 2.42 |  | 7.018 | sqm
| Wall 2 |  | 3 | 2.79 |  | 8.37 | sqm
| Wall 3 |  | 2.9 | 2.36 |  | 6.844 | sqm
| Wall 4 |  | 3 | 2.79 |  | 8.37 | sqm
Toilet 1
| Wall 1 |  | 1.8 | 2.83 |  | 5.094 | sqm
| Wall 2 |  | 1.8 | 2.83 |  | 5.094 | sqm
| Wall 3 |  | 1.8 | 2.52 |  | 4.536 | sqm
| Wall 4 |  | 1.8 | 2.83 |  | 5.094 | sqm
In Isolation Ward 2
Main ward
| Wall 1 |  | 10.41 | 3.21 |  | 33.4161 | sqm
| Wall 2 |  | 4.98 | 3.67 |  | 18.2766 | sqm
| Wall 3 |  | 10.41 | 3.21 |  | 33.4161 | sqm
| Wall 4 |  | 4.98 | 3.67 |  | 18.2766 | sqm
Room 1
| Wall 1 |  | 3.14 | 3.21 |  | 10.0794 | sqm
| Wall 2 |  | 4.97 | 3.67 |  | 18.2399 | sqm
| Wall 3 |  | 3.14 | 3.21 |  | 10.0794 | sqm
| Wall 4 |  | 4.97 | 3.67 |  | 18.2399 | sqm
Room 2
| Wall 1 |  | 1.8 | 2.42 |  | 4.356 | sqm
| Wall 2 |  | 2 | 2.4 |  | 4.8 | sqm
| Wall 3 |  | 1.8 | 2.42 |  | 4.356 | sqm
| Wall 4 |  | 2 | 1.96 |  | 3.92 | sqm
Toilet
| Wall 1 |  | 2.12 | 3.18 |  | 6.7416 | sqm
| Wall 2 |  | 2.45 | 3.09 |  | 7.5705 | sqm
| Wall 3 |  | 1.34 | 3 |  | 4.02 | sqm
| Wall 4 |  | 2.81 | 2.93 |  | 8.2333 | sqm
| Wall 5 |  | 3.46 | 3.18 |  | 11.0028 | sqm
| Wall 6 |  | 5.28 | 3.32 |  | 17.5296 | sqm
| For drain work |  |  |  |  | 50 | sqm
| Total a |  |  |  |  | 447.6158 | sqm
Deductions
In Isolation Ward 1
| Door 1 | 2 | 1.37 | 2.02 |  | 5.5348 | sqm
| Door 2 | 1 | 0.89 | 1.84 |  | 1.6376 | sqm
| Door 3 | 1 | 0.69 | 2.04 |  | 1.4076 | sqm
| Door 4 | 1 | 0.66 | 2.04 |  | 1.3464 | sqm
| Window 1 | 4 | 0.86 | 1 |  | 3.44 | sqm
| Window 2 | 1 | 0.66 | 0.8 |  | 0.528 | sqm
| Ventilator 1 | 1 | 0.56 | 0.43 |  | 0.2408 | sqm
| Ventilator 2 | 2 | 0.57 | 0.53 |  | 0.6042 | sqm
In Isolation Ward 2
| Door 1 | 2 | 1.37 | 2.31 |  | 6.3294 | sqm
| Door 2 | 2 | 0.66 | 2.18 |  | 2.8776 | sqm
| Window 1 | 3 | 1.11 | 1.4 |  | 4.662 | sqm
| Window 2 | 3 | 0.56 | 1.34 |  | 2.2512 | sqm
| Ventilator 1 | 1 | 0.87 | 0.6 |  | 0.522 | sqm
| Ventilator 2 | 1 | 0.63 | 0.38 |  | 0.2394 | sqm
| Ventilator 3 | 4 | 0.73 | 0.43 |  | 1.2556 | sqm
| Total b |  |  |  |  | 32.8766 | sqm
| Total (a-b) |  |  |  |  | 414.7392 | sqm
| At different location as per structure demand |  |  |  |  | 35.26 | sqm
| Total |  |  |  |  | 449.9992 | sqm
| taking 50% quantity |  |  |  |  | 224.9996 | sqm
B7 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. Two coats
| Total quantity |  |  |  |  | 300 | sqm
B8 | Providing and fixing approved quality natural stone cladding of 18–25 mm thickness, in required sizes, shapes, and patterns, on walls, columns, or façade surfaces, as per drawings, specifications, and as directed by the Engineer-in-Charge.
| Total quantity |  |  |  |  | 110 | sqm
B9 | Structural steel work in single section, fixed with or without connecting plate, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. Heavy weight grating made with equal leg angle frame of 40x40x5 and Shutter of 35x35x5 ms angle with Ms flat (30x5)mm at top . the spacing between ms flat is 50mm dimensions, total weight of cover and frame to be not less than 30 kg
For drain
| 1) |  | 12.77 |  | 30 | 383.1 | kg
| 2) |  | 19.44 |  | 30 | 583.2 | kg
| 3) |  | 6.98 |  | 30 | 209.4 | kg
| 4) |  | 24.06 |  | 30 | 721.8 | kg
| 5) |  | 6.55 |  | 30 | 196.5 | kg
| 6) |  | 21.36 |  | 30 | 640.8 | kg
| 7) |  | 2.81 |  | 30 | 84.3 | kg
| 8) |  | 10.32 |  | 30 | 309.6 | kg
| 9) |  | 12.73 |  | 30 | 381.9 | kg
| At different location as per structure demand |  |  |  |  | 189.4 | kg
| Total |  |  |  |  | 3700 | kg
B10 | Providing and laying 4" x 4" Polycrete pavers of dark gray and medium gray shades (as per sample approved) over a prepared base in cement mortar 1:4 (1 part cement : 4 parts coarse sand), including preparation of base, leveling, laying in approved pattern, filling of joints with fine sand/cement slurry, compacting, and curing, complete as per drawing and direction of the Engineer-in-Charge.
| 1 |  | 1.85 | 6.53 |  | 12.0805 | sqm
| 2 |  | 2.05 | 2.75 |  | 5.6375 | sqm
| 3 |  | 6.24 | 5.48 |  | 34.1952 | sqm
| 4 |  | 1.95 | 2.81 |  | 5.4795 | sqm
| At different location as per structure demand |  |  |  |  | 12.61 | sqm
| Total |  |  |  |  | 70.0027 | sqm
B11 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished seamless type tubes
For Isolation Ward 1
| 200x200x4MM | 11 | 0.12 |  | 25.27 | 33.3564 | kg
| Steel Plate(3mm thick) | 11 | 0.15 | 0.09 | 23.55 | 3.4972 | kg
| 100x100x3MM | 11 | 1.6 |  | 9.1 | 14.56 | kg
For Isolation Ward 2
| 200x200x4MM | 9 | 0.12 |  | 25.27 | 27.2916 | kg
| Steel Plate(3mm thick) | 9 | 0.15 | 0.09 | 23.55 | 2.8613 | kg
| 100x100x3MM | 9 | 1.75 |  | 9.1 | 15.925 | kg
For Passage
| 200x200x4MM | 6 | 0.12 |  | 25.27 | 18.1944 | kg
| Steel Plate(3mm thick) | 6 | 0.15 | 0.09 | 23.55 | 1.9076 | kg
| 100x100x3MM | 6 | 1.75 |  | 9.1 | 15.925 | kg
| At different location as per structure demand |  |  |  |  | 66.48 | kg
| Total |  |  |  |  | 199.9984 | kg
B12 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : 25 mm thick
Isolation Ward 1
| Main ward |  | 13.7 | 3 |  | 41.1 | sqm
| Room 1 |  | 3.7 | 2.6 |  | 9.62 | sqm
| Verandah |  | 21.18 | 1.5 |  | 31.77 | sqm
Isolation Ward 2
| Main ward |  | 10.41 | 4.98 |  | 51.8418 | sqm
| Room 1 |  | 3.14 | 4.97 |  | 15.6058 | sqm
|  |  | 18.24 | 1.5 |  | 27.36 | sqm
| At different location as per structure demand |  |  |  |  | 22.7 | sqm
| Total |  |  |  |  | 199.9976 | sqm
B13 | Kota stone slabs 20 mm thick in risers of steps, skirting, dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement: 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slabs, including rubbing and polishing complete.
Isolation Ward 1
| 1 |  | 20.78 | 0.15 |  | 3.117 | sqm
| 2 |  | 10.11 | 0.15 |  | 1.5165 | sqm
| 3 |  | 11.1 | 0.15 |  | 1.665 | sqm
| 4 |  | 11.1 | 0.15 |  | 1.665 | sqm
| 5 |  | 22.99 | 0.15 |  | 3.4485 | sqm
| 6 |  | 0.89 | 0.24 |  | 0.2136 | sqm
Isolation Ward 2
| 1 |  | 28.8 | 0.15 |  | 4.32 | sqm
| 2 |  | 14.53 | 0.15 |  | 2.1795 | sqm
| 3 |  | 15.5 | 0.15 |  | 2.325 | sqm
| At different location as per structure demand |  |  |  |  | 4.55 | sqm
| Total |  |  |  |  | 25.0001 | sqm
B14 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm(thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), Jointing with grey cement slurry @ 3.3 kg/sqm including pointing the joints with white cement and matching pigment etc., complete.
For walls
Isolation Ward 1
| 1 |  | 1.8 | 1.8 |  | 3.24 | sqm
| 2 |  | 2.9 | 3 |  | 8.7 | sqm
Isolation Ward 2
| 1 |  | 1.8 | 2 |  | 3.6 | sqm
| 2 |  | 2.12 | 2.46 |  | 5.2152 | sqm
| 3 |  | 3.46 | 2.81 |  | 9.7226 | sqm
For walls
Isolation Ward 1
Toilet
| Wall 1 |  | 2.9 | 2.3 |  | 6.67 | sqm
| Wall 2 |  | 3 | 2.3 |  | 6.9 | sqm
| Wall 3 |  | 2.9 | 2.3 |  | 6.67 | sqm
| Wall 4 |  | 3 | 2.3 |  | 6.9 | sqm
Toilet 1
| Wall 1 |  | 1.8 | 2.3 |  | 4.14 | sqm
| Wall 2 |  | 1.8 | 2.3 |  | 4.14 | sqm
| Wall 3 |  | 1.8 | 2.3 |  | 4.14 | sqm
| Wall 4 |  | 1.8 | 2.3 |  | 4.14 | sqm
Isolation Ward 2
Room 2
| Wall 1 |  | 1.8 | 2.3 |  | 4.14 | sqm
| Wall 2 |  | 2 | 2.3 |  | 4.6 | sqm
| Wall 3 |  | 1.8 | 2.3 |  | 4.14 | sqm
| Wall 4 |  | 2 | 2.3 |  | 4.6 | sqm
Toilet
| Wall 1 |  | 2.12 | 2.3 |  | 4.876 | sqm
| Wall 2 |  | 2.45 | 2.3 |  | 5.635 | sqm
| Wall 3 |  | 1.34 | 2.3 |  | 3.082 | sqm
| Wall 4 |  | 2.81 | 2.3 |  | 6.463 | sqm
| Wall 5 |  | 3.46 | 2.3 |  | 7.958 | sqm
| Wall 6 |  | 5.28 | 2.3 |  | 12.144 | sqm
| At different location as per structure demand |  |  |  |  | 18.18 | sqm
| Total |  |  |  |  | 149.9958 | sqm
B15 | Providing & Fixing double skin full height 12 mm thick solid partition of make STYLAM or similar (upto the 7 feet), vertical members to be fixed on the SS plate and caping on the floor. Approved BWR ply as per IS:303, finished both side with approved 1 mm laminate surface complete with door shutter with laminate finish matching to the other available side of the partition, to be incorporated with necessary hinges, sliding bolt from inside, handle and all complete as per design, direction and approval of the Engineer.
| Total quantity |  |  |  |  | 30 | sqm
B16 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length (hold fast lugs or dash fastener shall be paid for separately). Sal wood
| At different location as per structure demand |  |  |  |  | 0.5 | cum
B17 | Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows, fixing with butt hinges of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. (Note: Butt hinges and necessary screws shall be paid separately) Second class teak wood
| At different location as per structure demand |  |  |  |  | 30 | sqm
B18 | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick.
a | Second class teak wood |  |  |  |  | 20 | sqm
b | Float glass panes-4 mm thick glass pane (weight not less than 10 kg/sqm). |  |  |  |  | 10 | sqm
C. Roofing works
C1 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer onboth side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required.
| Total Quantity |  |  |  |  | 331.76 | sqm
| At different location as per structure demand |  |  |  |  | 18.24 | sqm
| Total |  |  |  |  | 350 | sqm
C2 | Providing and fixing precoated galvanised steel sheet roofing accessories of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05 mm) with Zinc coating 120 gram per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete :
C2.1 | Flashings/ Aprons.( Upto 600 mm)
| Total Quantity |  |  |  |  | 221.15 | metre |  | 240
18.85
| At different location as per structure demand |  |  |  |  | 18.85 | metre
| Total |  |  |  |  | 240 | metre
C2.2 | Gutter (600 mm over all girth)
| Total Quantity |  |  |  |  | 93 | metre
| At different location as per structure demand |  |  |  |  | 7 | metre
| Total |  |  |  |  | 100 | metre
C3 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete.
For Isolation Ward 1
|  | 15 | 5.36 |  | 4.4 | 353.76 | kg
|  | 15 | 0.48 |  | 4.4 | 2.112 | kg
|  | 15 | 2.96 |  | 4.4 | 13.024 | kg
|  | 13 | 1.54 |  | 4.4 | 6.776 | kg
For Isolation Ward 2
|  | 11 | 5.39 |  | 4.4 | 23.716 | kg
|  | 16 | 2.41 |  | 4.4 | 10.604 | kg
|  | 8 | 4.32 |  | 4.4 | 19.008 | kg
|  | 5 | 2.41 |  | 4.4 | 10.604 | kg
For Passage
|  | 3 | 5.4 |  | 4.4 | 23.76 | kg
| At different location as per structure demand |  |  |  |  | 36.64 | kg
| Total |  |  |  |  | 500.004 | kg
D. Plumbing & Sanitary works
D1 | Providing and fixing white vitreous china extended wall mounting water closet of size 780x370x690 mm of approved shape including providing & fixing white vitreous china cistern with dual flush fitting, of flushing capacity 3 litre/ 6 litre (adjustable to 4 litre/ 8 litres), including seat cover, and cistern fittings, nuts, bolts and gasket etc complete.
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 3 |  |  |  | 3 | nos
| Total |  |  |  |  | 7 | nos
D2 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require: White Vitreous China Flat back wash basin size 450x 300 mm with single 15 mm C.P. brass pillar tap
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 5 | nos
D3 | Providing and fixing CP Brass 32 mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge.
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 5 | nos
D4 | Providing and fixing toilet paper holder : C.P. brass
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 3 |  |  |  | 3 | nos
| Total |  |  |  |  | 7 | nos
D5 | Providing and fixing Health faucet with 1 metre long Flexible tube and C.P. wall hook with PVC & SS Screws wherever required make and as per the direction of Engineer-in-charge.
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 3 |  |  |  | 3 | nos
| Total |  |  |  |  | 7 | nos
D6 | Providing and fixing of C.P. Soap dish complete as per instruction of Engineer-in-charge.
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 5 | nos
D7 | Providing and fixing C.P Towel Rail 600mm long fixed to PVC cleats with C.p brass screws including cutting and making good the walls wherever required.
In Isolation Ward 1
| Toilet | 1 |  |  |  | 1 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 4 | nos
D8 | Providing and fixing C.P Single lever concealed diverter and Bath spout for bath and shower with Button at Top complete as per direction of the Engineer-in-charge
In Isolation Ward 1
| Toilet | 1 |  |  |  | 1 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 3 | nos
D9 | Providing and Fixing Shower Head Over head rose shower with revoling joint ( with boday roation) & 115 mm long shower arm complete as directed by enginner in charge
In Isolation Ward 1
| Toilet | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 2 | nos
D10 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore
In Isolation Ward 1
| Toilet | 2 |  |  |  | 2 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 3 |  |  |  | 3 | nos
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 7 | nos
D11 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. 15 mm nominal bore
In Isolation Ward 1
| Toilet | 4 |  |  |  | 4 | nos
| Toilet 1 | 2 |  |  |  | 2 | nos
In Isolation Ward 2
| Room 2 | 2 |  |  |  | 2 | nos
| Toilet | 2 |  |  |  | 2 | nos
| Total |  |  |  |  | 10 | nos
D12 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 15 mm nominal bore
In Isolation Ward 1
| Toilet | 4 |  |  |  | 4 | nos
| Toilet 1 | 2 |  |  |  | 2 | nos
In Isolation Ward 2
| Room 2 | 2 |  |  |  | 2 | nos
| Toilet | 2 |  |  |  | 2 | nos
| Total |  |  |  |  | 10 | nos
D13 | Providing and fixing of C.P towel ring square/circular fixed to wooden cleats with C.P brass screws including cutting and making good the walls wherever required.
In Isolation Ward 1
| Toilet | 1 |  |  |  | 1 | nos
| Toilet 1 | 1 |  |  |  | 1 | nos
In Isolation Ward 2
| Room 2 | 1 |  |  |  | 1 | nos
| Toilet | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 4 | nos
D14 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings and fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc.
| 15 mm nominal dia Pipes |  |  |  |  | 100 | metre
| 20 mm nominal dia Pipes |  |  |  |  | 80 | metre
| 25 mm nominal dia Pipes |  |  |  |  | 80 | metre
| 32 mm nominal dia Pipes |  |  |  |  | 70 | metre
D15 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work
| 15 mm nominal dia Pipes |  |  |  |  | 150 | metre
| 20 mm nominal dia Pipes |  |  |  |  | 120 | metre
| 25 mm nominal dia Pipes |  |  |  |  | 60 | metre
| 32 mm nominal dia Pipes |  |  |  |  | 50 | metre
D16 | Providing and laying Non Pressure NP-3 class (Medium duty) R.C.C. pipes including collars/spigot jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of jointsetc. Complete 450 mm dia RCC pipes.
| For drains |  |  |  |  | 20 | rmt
D17 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5
| For drain and plinth protection |  |  |  |  | 2 | each
#REF!
E1 | Supply, Wiring, Testing & Commissioning for switch board controlled light points with 3 X 1.5sq.mm FRLS PVC insulated copper wire and earthing with 1.5 sq.mm. FRLS PVC insulated copper wire in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of modular switches as specified complete with modular plate with GI boxes of suitable as complete as required.
E1.1 | First Point (One point controlled by one no. 6 amps switch.) (Normal Light Point)
| Isolation ward 1 |  |  |  |  | 21 | Nos
| Isolation ward 2 |  |  |  |  | 18 | Nos
| Total |  |  |  |  | 39 | Nos
E1.2 | same as the above for Looping Point
| Isolation ward 1 |  |  |  |  | 6 | Nos
| Isolation ward 2 |  |  |  |  | 7 | Nos
| Total |  |  |  |  | 13 | Nos
E2 | Supply, Wiring, Testing & Commissioning for MCB controlled light points with 2 x 2.5 + 1 X 1.5 sq.mm FRLS PVC insulated copper wires in recessed / surface mounted in in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles, conduit fixing material, MS Connector, along with all required fittings. (Cost of MCB not to be included)
E2.1 | First Point (First light points controlled by one no.6A SP MCB)
| Isolation ward 1 |  |  |  |  | 6 | Nos
| Isolation ward 2 |  |  |  |  | 5 | Nos
| Total |  |  |  |  | 11 | Nos
E2.2 | same as above for the Looping Point
| Isolation ward 1 |  |  |  |  | 2 | Nos
| Isolation ward 2 |  |  |  |  | 3 | Nos
| Total |  |  |  |  | 5 | Nos
E3 | Supply, Wiring, Testing & Commissioning for 6 A multistandard shutterd switched socket outlet with 3 x 1.5 sq mm FRLS PVC insulated copper wire & earthing with 1.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of 6amps modular switch, socket complete with modular plate with suitable size of GI box complete in all respect.
| Isolation ward 1 |  |  |  |  | 16 | Nos
| Isolation ward 2 |  |  |  |  | 12 | Nos
| Total |  |  |  |  | 28 | Nos
E4 | Supply, Wiring, Testing & Commissioning for 1 nos, 16 A shuttered, switched socket outlets with 2 x4 +1 x 2.5 sq.mm FRLS PVC insulated copper wire & earthing with 2.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, including providing & fixing of 1 nos. of 16amps modular switched socket outlets alongwith 1nos 16 A switch with modular plate with GI box complete.
| Isolation ward 1 |  |  |  |  | 8 | Nos
| Isolation ward 2 |  |  |  |  | 8 | Nos
| Total |  |  |  |  | 16 | Nos
E5 | Supply and wiring of exhaust fan point with 3 X 1.5 sq.mm FRLS PVC insulated copper conductor cable in in surface / recessed GI conduit, fixing on surface or wall/ceiling including fixing of saddles etc. including galvanised M.S. box, modular range of plate switches, 6A socket, modular cover plate, PVC insulated copper earth wire etc. complete as required.
| Isolation ward 1 |  |  |  |  | 3 | Nos
| Isolation ward 2 |  |  |  |  | 4 | Nos
| Total |  |  |  |  | 7 | Nos
E6 | Wiring for the Ceiling fan points with 3X1.5 Sq.mm PVC insulated stranded copper conductor wires in concealed FRLS PVC. conduits in ceiling / walls as directed including providing Hexagonal fan Box , Electronic fan regulator,6 amp switch, 5 sided G.I. Boxes for housing the regulator and earthing complete as required.
| Isolation ward 1 |  |  |  |  | 4 | Nos
| Isolation ward 2 |  |  |  |  | 3 | Nos
| Total |  |  |  |  | 7 | Nos
E7 | Providing and fixing in position the following FRLS PVC conduits including all accessories concealed in F. ceiling (PVC conduit not to be instaUed above false ceilfng) /waif/ floor as required including M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl-ete with 1.6 mm dia G.I. pull wires in the length of conduit.
E7.1 | 20 mm dia conduit ( 1.6 mm thick) |  |  |  |  | 50 | metre
E7.2 | 25 mm dia conduit (1.6 mm thick) |  |  |  |  | 60 | metre
E7.3 | 32 mm dia conduit (2.0 mm thick) |  |  |  |  | 40 | metre
E8 | Supply,installing ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm-in proof, with hinged and lockable doors complete with DP MCB's and inter- connection with copper wire , insulated copper bus bar , cable glands-/conduit entry bushes, bonding to earth and paint-ing. Also provide separate neutral: busbar for each phase. Provide separate ,Earth Links for each phase. Use brass thimbles for connections of all: wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated.
E8.1 | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB.
| Total |  |  |  |  | 1 | nos
E8.2 | 8 Way TPN DB, each phase consisting of 6 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB.
| Total |  |  |  |  | 2 | nos
E8.3 | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB.
| Total |  |  |  |  | 1 | nos
E9 | Supply, Installation, Testing & Commissioning of 1200 mm dia 5 Star rated ceiling fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ).
| Isolation ward 1 |  |  |  |  | 4 | Nos
| Isolation ward 2 |  |  |  |  | 3 | Nos
| Total |  |  |  |  | 7 | Nos
E10 | Supply & Installation, Testing & Commissioning of 250 mm dia exhaust fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ).
| Isolation ward 1 |  |  |  |  | 3 | Nos
| Isolation ward 2 |  |  |  |  | 4 | Nos
| Total |  |  |  |  | 7 | Nos
E11 | Supplying of light fixtures as per sample approved.

## Abstract For Hospital
LSS__Bill of Quantities_Refurbishment of Hospital -Main Building_07.05.2026
Sr. No. | Item Description | Unit | Quantity | Rate | Amount | Reference
A.Dismantling & Demolishing
A1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge. | cum | 12.0032 |  | 0
A2 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead. For thickness of tiles 10 mm to 25 mm | sqm | 500.0006 |  | 0
A3 | Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of: G.S. Sheet | sqm | 1350 |  | 0
A4 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar | cum | 39.9969 |  | 0
A5 | Demolishing stone rubble masonry manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge : In lime mortar | cum | 30.0031 |  | 0
A5 | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead. | Each | 11 |  | 0
A6 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead. | sqm | 1449.998 |  | 0
A7 | Careful removal of existing wooden false ceiling, including all supporting framework, battens, and fixtures, ensuring minimum damage to adjoining surfaces; stacking of all serviceable material at designated location within site premises as directed by the Engineer-in-Charge. | L.S | 1
| Total A |  |  |  | 0
B. Masonry and Flooring & Wood Work
B1 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | cum | 12.0032 |  | 0
B2 | 40 mm thick fine dressed stone flooring over 20 mm (average) thick base of cement mortar 1:5 (1 cement : 5 coarse sand) with joints finished flush. White sand stone | sqm | 30 |  | 0
B3 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:4 (1 cement : 4 coarse sand) | cum | 61.9954 |  | 0
B4 | 12 mm cement plaster finished with a floating coat of neat cement of mix : 1:4 (1 cement: 4 fine sand) | sqm | 649.9976 |  | 0
B5 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. Two coats | sqm | 1500 |  | 0
B5 | Random rubble masonry with hard stone in superstructure above plinth level and upto floor five level, including leveling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) at window sills, ceiling level and the like. Cement mortar 1:6 (1 cement : 6 coarse sand) | cum | 30 |  | 0
B6 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : 25 mm thick | sqm | 700.0018 |  | 0
B7 | Kota stone slabs 20 mm thick in risers of steps, skirting, dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement: 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slabs, including rubbing and polishing complete. | sqm | 47.2482 |  | 0
B8 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm(thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), Jointing with grey cement slurry @ 3.3 kg/sqm including pointing the joints with white cement and matching pigment etc., complete. | sqm | 599.9963 |  | 0
B9 | Providing & Fixing double skin full height 12 mm thick solid partition of make STYLAM or similar (upto the 7 feet), vertical members to be fixed on the SS plate and caping on the floor. Approved BWR ply as per IS:303, finished both side with approved 1 mm laminate surface complete with door shutter with laminate finish matching to the other available side of the partition, to be incorporated with necessary hinges, sliding bolt from inside, handle and all complete as per design, direction and approval of the Engineer. | sqm | 30 |  | 0
B10 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length (hold fast lugs or dash fastener shall be paid for separately). Sal wood | cum | 1 |  | 0
B11 | Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows, fixing with butt hinges of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. (Note: Butt hinges and necessary screws shall be paid separately) Second class teak wood | sqm | 100 |  | 0
B12 | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick. |  |  |  | 0
a | Second class teak wood | sqm | 100 |  | 0
b | Float glass panes-4 mm thick glass pane (weight not less than 10 kg/sqm). | sqm | 40 |  | 0
B13 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished seamless type tubes | kg | 499.9976 |  | 0
B14 | Careful repair and refurbishment of existing wooden doors and windows, including minor dismantling, replacement of decayed wood with matching timber, tightening of joints, surface preparation, anti-termite treatment, repair/refixing of fittings, and replacement of broken or damaged glass panes where required, complete with polishing/painting as per engineer in charge. | L.S
| Total B |  |  |  | 0
C. Roofing works
C1 | Provide and fixing 19 mm thick marine plywood (water-resistant) onto rafters using suitable screws and washers, including all required fixing materials (nails, screws, washers, adhesives), aligning, leveling, cutting to fit at joints, and finishing. Work to be done complete, as per Engineer‑in‑Charge approval. | sqm | 1100 |  | 0
C2 | Providng and fixing insulated PUFF sheet Roofing with the following specificifications -Panel Specifications: Roof shall be made of sandwich panel, made out of 0.50mm colour coated galvalume steel sheets spec 150gsm & 550mpa as as outer & inner cladding will be 0.40 mm colour coated galvalume sheet sheet spec 150 gsm & 550 mpa on both side of PUFF. Make of the sheet to be OEM TATA/JSW PRIME material. . The total thickness of panel will be 50/80 mm for roof, panel PU foam will be CFC free , self-extinguishing, Fire resistance type having density of 40 kg/cum. The Panel are joined together by tongue & groove method, complete in all respect including all the accessories. Fixing Mechanism: The sheeting will be fixed using galvanized self-drilling, self-tapping fasteners with EPDM seals to ensure secure attachment and weatherproofing. | sqm | 1100 |  | 0
C3 | Providing and fixing flashings, Cappings, valleys manufactured same material as mentioned for roof sheets above in standard lengths of 2.5 mtr. And fixed by means of hex-head self-drilling stitching screws. 501 to 1000 mm Girth in Ridges, flashings, aprons, barge boards (Make of the sheet to be OEM TATA/JSW PRIME material) | rmt | 800 |  | 0
C4 | Providing and Fixing Gutters manufactured same material as mentioned for roof sheets without PUFF insultation above in standard lengths of 2.5 mtr. And fixed by means of hex-head self-drilling stitching screws. 501 to 1000 mm Girth (Make of the sheet to be OEM TATA/JSW PRIME material) | rmt | 439.9963 |  | 0
C5 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer onboth side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. | sqm | 140 |  | 0
C6 | Providing and fixing precoated galvanised steel sheet roofing accessories of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05 mm) with Zinc coating 120 gram per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete : Flashings/ Aprons.( Upto 600 mm) | metre | 140 |  | 0
C7 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | kg | 730.0036 |  | 0
| Total C |  |  |  | 0
D. Plumbing & Sanitary works
D1 | Providing and fixing white vitreous china extended wall mounting water closet of size 780x370x690 mm of approved shape including providing & fixing white vitreous china cistern with dual flush fitting, of flushing capacity 3 litre/ 6 litre (adjustable to 4 litre/ 8 litres), including seat cover, and cistern fittings, nuts, bolts and gasket etc complete. | Each | 13 |  | 0
D2 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require: White Vitreous China Flat back wash basin size 450x 300 mm with single 15 mm C.P. brass pillar tap | Each | 11 |  | 0
D3 | Providing and fixing CP Brass 32 mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge. | Each | 11 |  | 0
D4 | Providing and fixing toilet paper holder : C.P. brass | Each | 13 |  | 0
D5 | Providing and fixing Health faucet with 1 metre long Flexible tube and C.P. wall hook with PVC & SS Screws wherever required make and as per the direction of Engineer-in-charge. | Each | 13 |  | 0
D6 | Providing and fixing of C.P. Soap dish complete as per instruction of Engineer-in-charge. | Each | 9 |  | 0
D7 | Providing and fixing C.P Towel Rail 600mm long fixed to PVC cleats with C.p brass screws including cutting and making good the walls wherever required. | Each | 3 |  | 0
D8 | Providing and fixing C.P Single lever concealed diverter and Bath spout for bath and shower with Button at Top complete as per direction of the Engineer-in-charge | Each | 3 |  | 0
D9 | Providing and Fixing Shower Head Over head rose shower with revoling joint ( with boday roation) & 115 mm long shower arm complete as directed by enginner in charge | Each | 3 |  | 0
D10 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore | Each | 13 |  | 0
D11 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. 15 mm nominal bore | Each | 22 |  | 0
D12 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 15 mm nominal bore | Each | 22 |  | 0
D13 | Providing and fixing of C.P towel ring square/circular fixed to wooden cleats with C.P brass screws including cutting and making good the walls wherever required. | Each | 9 |  | 0
D14 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings and fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc.
| 15 mm nominal dia Pipes | metre | 100 |  | 0
| 20 mm nominal dia Pipes | metre | 80 |  | 0
| 25 mm nominal dia Pipes | metre | 80 |  | 0
| 32 mm nominal dia Pipes | metre | 70 |  | 0
D15 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work
| 15 mm nominal dia Pipes | metre | 150 |  | 0
| 20 mm nominal dia Pipes | metre | 120 |  | 0
| 25 mm nominal dia Pipes | metre | 60 |  | 0
| 32 mm nominal dia Pipes | metre | 50 |  | 0
D16 | Providing and laying Non Pressure NP-3 class (Medium duty) R.C.C. pipes including collars/spigot jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of jointsetc. Complete 450 mm dia RCC pipes. | rmt | 20 |  | 0
D17 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | each | 2 |  | 0
| Total D |  |  |  | 0
E.Electrical Work
Point Wiring: Point wiring rates are inclusive of 2X2.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit and 1.5 sq mm FRLS PVC insulated copper conductor insulated earth wire.
E1 | Supply, Wiring, Testing & Commissioning for switch board controlled light points with 3 X 1.5sq.mm FRLS PVC insulated copper wire and earthing with 1.5 sq.mm. FRLS PVC insulated copper wire in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of modular switches as specified complete with modular plate with GI boxes of suitable as complete as required.
E1.1 | First Point (One point controlled by one no. 6 amps switch.) (Normal Light Point) | Nos | 156 |  | 0
E1.2 | same as the above for Looping Point | Nos | 24 |  | 0
E2 | Supply, Wiring, Testing & Commissioning for MCB controlled light points with 2 x 2.5 + 1 X 1.5 sq.mm FRLS PVC insulated copper wires in recessed / surface mounted in in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles, conduit fixing material, MS Connector, along with all required fittings. (Cost of MCB not to be included)
E2.1 | First Point (First light points controlled by one no.6A SP MCB) | Nos | 40 |  | 0
E2.2 | same as above for the Looping Point | Nos | 7 |  | 0
E3 | Supply, Wiring, Testing & Commissioning for 6 A multistandard shutterd switched socket outlet with 3 x 1.5 sq mm FRLS PVC insulated copper wire & earthing with 1.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of 6amps modular switch, socket complete with modular plate with suitable size of GI box complete in all respect. | Nos | 90 |  | 0
E4 | Supply, Wiring, Testing & Commissioning for 1 nos, 16 A shuttered, switched socket outlets with 2 x4 +1 x 2.5 sq.mm FRLS PVC insulated copper wire & earthing with 2.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, including providing & fixing of 1 nos. of 16amps modular switched socket outlets alongwith 1nos 16 A switch with modular plate with GI box complete. | Pt. | 54 |  | 0
E5 | Wiring for projector/Geyser points with 2 x 4 + 1 x 2.5 sq mm FRLS PVC insulated strande·d copper con-ductor wires in concealed FRLS PVC conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switch near the white board and 16 amps 5 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuits) | Pt. | 9 |  | 0
E6 | Wiring for A/C outlet points with 2X4.0+1X2.5 sq mm FRLS PVC insulated stranded copper conductor wires in FRLS PVC conduit/wall/floor ducts as directed including 25 A single phase Triny type socket with 25 A SP MCB (motor duty), 2 mm thick providing and Nos. fixing M.S. box to house the above duly painted and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required. | Pt. | 10 |  | 0
E7 | Supply and wiring of exhaust fan point with 3 X 1.5 sq.mm FRLS PVC insulated copper conductor cable in in surface / recessed GI conduit, fixing on surface or wall/ceiling including fixing of saddles etc. including galvanised M.S. box, modular range of plate switches, 6A socket, modular cover plate, PVC insulated copper earth wire etc. complete as required. | Nos | 17 |  | 0
E8 | Wiring for the Ceiling fan points with 3X1.5 Sq.mm PVC insulated stranded copper conductor wires in concealed FRLS PVC. conduits in ceiling / walls as directed including providing Hexagonal fan Box , Electronic fan regulator,6 amp switch, 5 sided G.I. Boxes for housing the regulator and earthing complete as required. | Nos | 41 |  | 0
E9 | Providing and fixing in position the following FRLS PVC conduits including all accessories concealed in F. ceiling (PVC conduit not to be instaUed above false ceilfng) /waif/ floor as required including M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl-ete with 1.6 mm dia G.I. pull wires in the length of conduit.
E9.1 | 20 mm dia conduit ( 1.6 mm thick) | rmt | 150 |  | 0
E9.2 | 25 mm dia conduit (1.6 mm thick) | rmt | 80 |  | 0
E9.3 | 32 mm dia conduit (2.0 mm thick) | rmt | 65 |  | 0
E10 | Supply,installing ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm-in proof, with hinged and lockable doors complete with DP MCB's and inter- connection with copper wire , insulated copper bus bar , cable glands-/conduit entry bushes, bonding to earth and paint-ing. Also provide separate neutral: busbar for each phase. Provide separate ,Earth Links for each phase. Use brass thimbles for connections of all: wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated.
E10.1 | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB. | nos | 5 |  | 0
E10.2 | 8 Way TPN DB, each phase consisting of 6 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB. | nos | 4 |  | 0
E10.3 | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB. | nos | 4 |  | 0
E11 | Supply & Installation, Testing & Commissioning of 250 mm dia exhaust fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ). | Each | 17 |  | 0
E12 | Supply, Installation, Testing & Commissioning of 1200 mm dia 5 Star rated ceiling fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ). | Each | 41 |  | 0
E13 | Supplying of light fixtures as per sample approved. | L.S
| Total E |  |  |  | 0
| Total (A+B+C+D+E) |  |  |  | 0
| Grand Total |  |  |  | 0

## Measurement Sheet For Hospital
LSS__Takeoff sheet_Refurbishment of Hospital -Main Building_07.05.2026
S.N0 | Item Description | Nos | L | W | H/D | Qty. | Unit
A.Dismantling & Demolishing
A1 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge.
| Boys Ward (A30) |  | 12.19 | 6.09 | 0.1 | 7.4237 | cum
| Lobby (A21) |  | 2.355 | 6.09 | 0.1 | 1.4342 | cum
| Girls Ward (A22) |  | 11.92 | 6.09 | 0.1 | 7.2593 | cum
| Isolation Ward (A32,33,34) |  | 8.59 | 2.92 | 0.1 | 2.5083 | cum
| Store (A31) |  | 1.815 | 2.63 | 0.1 | 0.47734 | cum
| Staff Ward (A37) |  | 2.64 | 3.84 | 0.1 | 1.0138 | cum
| Female Isolation Ward (A26,27,28) |  | 7.4 | 2.96 | 0.1 | 2.1904 | cum
| Store (A29) |  | 3.2 | 1.5 | 0.1 | 0.48 | cum
| Female Staff Ward (A23) |  | 2.8 | 4.1 | 0.1 | 1.148 | cum
| OPD (A11) |  | 2.8 | 3.1 | 0.1 | 0.868 | cum
| Consultation Room (A12) |  | 3.9 | 3.1 | 0.1 | 1.209 | cum
| Observation Room (A13) |  | 4.155 | 3.1 | 0.1 | 1.2881 | cum
| Duty Room (A14) |  | 4.2 | 5.6 | 0.1 | 2.352 | cum
| Store (A16) |  | 2.09 | 1.4 | 0.1 | 0.2926 | cum
| Emergency room (A15) |  | 2.03 | 1.445 | 0.1 | 0.29334 | cum
| Emergency room (A17) |  | 2.71 | 2.03 | 0.1 | 0.55013 | cum
| Foyer (A19) |  | 1.775 | 1.28 | 0.1 | 0.2272 | cum
| Dining Hall (A20) |  | 10.94 | 2.99 | 0.1 | 3.2711 | cum
| Physiotherapy Chamber (A10) |  | 2.7 | 2.62 | 0.1 | 0.7074 | cum
| Minor OT (A9) |  | 2.78 | 2.86 | 0.1 | 0.79508 | cum
| Waiting Room (A2) |  | 2.79 | 4.22 | 0.1 | 1.1774 | cum
| RMO's Chamber (A3) |  | 2.78 | 4.22 | 0.1 | 1.1732 | cum
| Office Reception (A1) |  | 2.895 | 1.56 | 0.1 | 0.45162 | cum
| Office Reception (A1) |  | 2.895 | 0.5 | 0.45 | 0.65138 | cum
| X-Ray room (A4) |  | 5.2 | 3.3 | 0.1 | 1.716 | cum
| Test Lab (A5) |  | 4.54 | 3.3 | 0.1 | 1.4982 | cum
| Dispensary (A6) |  | 4.5 | 3.19 | 0.1 | 1.4355 | cum
| Medical Store (A7) |  | 4.37 | 3.1 | 0.1 | 1.3547 | cum
| Toilet (A18) |  | 1.005 | 2.01 | 0.1 | 0.202 | cum
| Toilet (A25) |  | 2.76 | 2.96 | 0.1 | 0.81696 | cum
| Toilet (A28.1) |  | 1.28 | 2.92 | 0.1 | 0.37376 | cum
| Toilet (A35) |  | 2.75 | 2.65 | 0.1 | 0.72875 | cum
| Toilet (A38) |  | 1.16 | 2.99 | 0.1 | 0.34684 | cum
| Toilet (B9) |  | 1.47 | 2.51 | 0.1 | 0.36897 | cum
| Toilet (A7.1) |  | 1.5 | 3.1 | 0.1 | 0.465 | cum
| Toilet (A23.1) |  | 3 | 1.7 | 0.1 | 0.51 | cum
| Toilet (A30.1) |  | 2.52 | 1.58 | 0.1 | 0.39816 | cum
0
| Bath (A32) |  | 2.64 | 2.885 | 0.1 | 0.76164 | cum
| Bath (24.1) |  | 1.835 | 2.71 | 0.1 | 0.49729 | cum
| Total |  |  |  |  | 50.7161 | cum
| 20% of total quantity to be taken |  |  |  |  | 10.1432 | cum
| At different location as per structure demand |  |  |  |  | 1.86 | cum
| Total |  |  |  |  | 12.0032 | cum
A2 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead. For thickness of tiles 10 mm to 25 mm
| Boys Ward (A30) |  | 12.19 | 6.09 |  | 74.2371 | sqm
| Lobby (A21) |  | 2.355 | 6.09 |  | 14.3419 | sqm
| Girls Ward (A22) |  | 11.92 | 6.09 |  | 72.5928 | sqm
| Isolation Ward (A32,33,34) |  | 8.59 | 2.92 |  | 25.0828 | sqm
| Staff Ward (A37) |  | 2.64 | 3.84 |  | 10.1376 | sqm
| Female Isolation Ward (A26,27,28) |  | 7.4 | 2.96 |  | 21.904 | sqm
| Female Staff Ward (A23) |  | 2.8 | 4.1 |  | 11.48 | sqm
| OPD (A11) |  | 2.8 | 3.1 |  | 8.68 | sqm
| Consultation Room (A12) |  | 3.9 | 3.1 |  | 12.09 | sqm
| Duty Room (A14) |  | 4.2 | 5.6 |  | 23.52 | sqm
| Emergency room (A15) |  | 2.03 | 1.445 |  | 2.9333 | sqm
| Emergency room (A17) |  | 2.71 | 2.03 |  | 5.5013 | sqm
| Foyer (A19) |  | 1.775 | 1.28 |  | 2.272 | sqm
| Dining Hall (A20) |  | 10.94 | 2.99 |  | 32.7106 | sqm
| Physiotherapy Chamber (A10) |  | 2.7 | 2.62 |  | 7.074 | sqm
| Minor OT (A9) |  | 2.78 | 2.86 |  | 7.9508 | sqm
| Waiting Room (A2) |  | 2.79 | 4.22 |  | 11.7738 | sqm
| RMO's Chamber (A3) |  | 2.78 | 4.22 |  | 11.7316 | sqm
| Office Reception (A1) |  | 2.895 | 1.56 |  | 4.5162 | sqm
| X-Ray room (A4) |  | 5.2 | 3.3 |  | 17.16 | sqm
| Medical Store (A7) |  | 4.37 | 3.1 |  | 13.547 | sqm
| Toilet (A18) |  | 1.005 | 2.01 |  | 2.02 | sqm
| Toilet (A25) |  | 2.76 | 2.96 |  | 8.1696 | sqm
| Toilet (A28.1) |  | 1.28 | 2.92 |  | 3.7376 | sqm
| Toilet (A35) |  | 2.75 | 2.65 |  | 7.2875 | sqm
| Toilet (A38) |  | 1.16 | 2.99 |  | 3.4684 | sqm
| Toilet (B9) |  | 1.47 | 2.51 |  | 3.6897 | sqm
| Toilet (A7.1) |  | 1.5 | 3.1 |  | 4.65 | sqm
| Toilet (A23.1) |  | 3 | 1.7 |  | 5.1 | sqm
| Toilet (A30.1) |  | 2.52 | 1.58 |  | 3.9816 | sqm
0
| Bath (A32) |  | 2.64 | 2.885 |  | 7.6164 | sqm
| Bath (24.1) |  | 1.835 | 2.71 |  | 4.9729 | sqm
| At different location as per structure demand |  |  |  |  | 54.07 | sqm
| Total |  |  |  |  | 500.0006 | sqm
A3 | Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material within 50 metres lead of: G.S. Sheet
| Hospital Area |  |  |  |  | 1298.28 | sqm
| At different location as per structure demand |  |  |  |  | 51.72 | sqm
| Total |  |  |  |  | 1350 | sqm
A4 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar
Hospital Area
| 1 | 2 | 1.41 | 0.23 | 2.1 | 1.3621 | cum
| 2 | 1 | 0.74 | 0.23 | 2.1 | 0.35742 | cum
| 3 | 2 | 2.15 | 0.09 | 2.44 | 0.94428 | cum
| 4 | 1 | 3.09 | 0.09 | 2.7 | 0.75087 | cum
| 5 | 1 | 0.88 | 0.11 | 2.64 | 0.25555 | cum
| 6 | 2 | 1 | 0.1 | 2.64 | 0.528 | cum
| 7 | 1 | 1.21 | 0.1 | 2.64 | 0.31944 | cum
| 8 | 2 | 1.5 | 0.16 | 2.72 | 1.3056 | cum
| 9 | 2 | 2.96 | 0.15 | 2.72 | 2.4154 | cum
| 10 | 2 | 3.08 | 0.11 | 2.72 | 1.8431 | cum
| 11 | 2 | 1.14 | 0.17 | 2.64 | 1.0233 | cum
| 12 | 1 | 0.8 | 0.28 | 4.56 | 1.0214 | cum
| 13 | 2 | 3.38 | 0.3 | 4.53 | 9.1868 | cum
| 14 | 1 | 0.82 | 0.23 | 2.1 | 0.39606 | cum
| 15 | 1 | 0.52 | 0.13 | 2.2 | 0.14872 | cum
| 16 | 1 | 2.08 | 0.11 | 2.86 | 0.65437 | cum
| 17 | 1 | 0.62 | 0.27 | 4.445 | 0.74409 | cum
| 18 | 1 | 1.315 | 0.28 | 2.975 | 1.0954 | cum
| 19 | 1 | 5.11 | 0.23 | 1.827 | 2.1473 | cum
| 20 | 1 | 6.35 | 0.475 | 2.48 | 7.4803 | cum
| 21 | 1 | 1.06 | 0.33 | 2.48 | 0.8675 | cum
| At different location as per structure demand |  |  |  |  | 5.15 | cum
| Total |  |  |  |  | 39.9969 | cum
A5 | Demolishing stone rubble masonry manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge : In lime mortar
Hospital Area
| 1 | 1 | 1.2 | 0.76 | 2.4 | 2.1888 | cum
| 2 | 1 | 1.34 | 0.69 | 2.4 | 2.219 | cum
| 3 | 1 | 0.9 | 0.66 | 2.4 | 1.4256 | cum
| 4 | 2 | 1.34 | 0.66 | 2.4 | 4.2451 | cum
| 5 | 1 | 0.89 | 0.665 | 2.1 | 1.2429 | cum
| 6 | 2 | 0.68 | 0.48 | 4.445 | 2.9017 | cum
Steps
| 1 |  |  |  |  | 9.81 | cum
| 2 |  |  |  |  | 2.18 | cum
| 3 |  |  |  |  | 0.35 | cum
| 4 |  |  |  |  | 0.11 | cum
| 5 |  |  |  |  | 0.22 | cum
| At different location as per structure demand |  |  |  |  | 3.11 | cum
| Total |  |  |  |  | 30.0031 | cum
A5 | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead.
| Toilet 1 | 4 |  |  |  | 4 | nos
| Toilet 2 | 3 |  |  |  | 3 | nos
| Toilet 3 | 1 |  |  |  | 1 | nos
| Toilet 4 | 1 |  |  |  | 1 | nos
| Toilet 5 | 1 |  |  |  | 1 | nos
| Toilet 6 | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 11 | nos
A6 | Dismantling old plaster or skirting raking out joints and cleaning the surface for plaster including disposal of rubbish to the dumping ground within 50 metres lead.
Boys Ward (A30)
| Wall 1 |  | 12.19 | 4.56 |  | 55.5864 | sqm
| Wall 2 |  | 6.09 | 5.95 |  | 36.2355 | sqm
| Wall 3 |  | 12.19 | 4.56 |  | 55.5864 | sqm
| Wall 4 |  | 6.09 | 5.95 |  | 36.2355 | sqm
Lobby (A21)
| Wall 1 |  | 2.355 | 4.56 |  | 10.7388 | sqm
| Wall 2 |  | 6.09 | 5.95 |  | 36.2355 | sqm
| Wall 3 |  | 2.39 | 4.56 |  | 10.8984 | sqm
| Wall 4 |  | 6.09 | 5.95 |  | 36.2355 | sqm
Girls Ward (A22)
| Wall 1 |  | 11.915 | 4.56 |  | 54.3324 | sqm
| Wall 2 |  | 6.09 | 5.95 |  | 36.2355 | sqm
| Wall 3 |  | 11.92 | 4.56 |  | 54.3552 | sqm
| Wall 4 |  | 6.09 | 5.95 |  | 36.2355 | sqm
Isolation Ward (A32,33,34)
| Wall 1 |  | 8.59 | 4.56 |  | 39.1704 | sqm
| Wall 2 |  | 2.92 | 3.41 |  | 9.9572 | sqm
| Wall 3 |  | 8.59 | 2.72 |  | 23.3648 | sqm
| Wall 4 |  | 1.04 | 3.41 |  | 3.5464 | sqm
Store (A31)
| Wall 1 |  | 2.63 | 4.56 |  | 11.9928 | sqm
| Wall 2 |  | 1.82 | 3.41 |  | 6.2062 | sqm
| Wall 3 |  | 2.63 | 3.41 |  | 8.9683 | sqm
Staff Ward (A37)
| Wall 1 |  | 2.64 | 4.56 |  | 12.0384 | sqm
| Wall 2 |  | 3.84 | 5.95 |  | 22.848 | sqm
| Wall 3 |  | 3.84 | 5.95 |  | 22.848 | sqm
Female Isolation Ward (A26,27,28)
| Wall 1 |  | 7.51 | 2.72 |  | 20.4272 | sqm
| Wall 2 |  | 2.96 | 3.41 |  | 10.0936 | sqm
| Wall 3 |  | 7.51 | 4.56 |  | 34.2456 | sqm
Store (A29)
| Wall 1 |  | 2.91 | 4.56 |  | 13.2696 | sqm
| Wall 2 |  | 1.59 | 3.41 |  | 5.4219 | sqm
| Wall 3 |  | 3.27 | 3.41 |  | 11.1507 | sqm
| Wall 4 |  | 1.59 | 3.41 |  | 5.4219 | sqm
Female Staff Ward (A23)
| Wall 1 |  | 2.71 | 4.56 |  | 12.3576 | sqm
| Wall 2 |  | 4.14 | 5.95 |  | 24.633 | sqm
| Wall 3 |  | 4.14 | 5.95 |  | 24.633 | sqm
OPD (A11)
| Wall 1 |  | 4.16 | 4.56 |  | 18.9696 | sqm
| Wall 2 |  | 3.08 | 3.37 |  | 10.3796 | sqm
Consultation Room (A12)
| Wall 1 |  | 2.85 | 4.56 |  | 12.996 | sqm
Observation Room (A13)
| Wall 1 |  | 4.15 | 4.56 |  | 18.924 | sqm
| Wall 2 |  | 3.08 | 3.37 |  | 10.3796 | sqm
Duty Room (A14)
| Wall 1 |  | 4.27 | 4.56 |  | 19.4712 | sqm
| Wall 2 |  | 5.63 | 3.37 |  | 18.9731 | sqm
| Wall 3 |  | 4.27 | 4.43 |  | 18.9161 | sqm
| Wall 4 |  | 5.63 | 3.37 |  | 18.9731 | sqm
Store (A16)
| Wall 1 |  | 1.92 | 4.43 |  | 8.5056 | sqm
| Wall 2 |  | 1.38 | 4.43 |  | 6.1134 | sqm
| Wall 3 |  | 1.25 | 4.43 |  | 5.5375 | sqm
| Wall 4 |  | 0.52 | 4.43 |  | 2.3036 | sqm
Foyer (A19)
| Wall 1 |  | 1.78 | 4.43 |  | 7.8854 | sqm
| Wall 2 |  | 1.28 | 4.43 |  | 5.6704 | sqm
| Wall 3 |  | 1.78 | 4.43 |  | 7.8854 | sqm
| Wall 4 |  | 1.28 | 4.43 |  | 5.6704 | sqm
Emergency room (A15)
| Wall 1 |  | 2.03 | 4.43 |  | 8.9929 | sqm
| Wall 2 |  | 1.44 | 4.43 |  | 6.3792 | sqm
| Wall 3 |  | 1.44 | 4.43 |  | 6.3792 | sqm
Emergency room (A17)
| Wall 1 |  | 2.03 | 4.43 |  | 8.9929 | sqm
| Wall 2 |  | 2.71 | 4.43 |  | 12.0053 | sqm
| Wall 3 |  | 2.71 | 4.43 |  | 12.0053 | sqm
Dining Hall (A20)
| Wall 1 |  | 10.94 | 4.56 |  | 49.8864 | sqm
| Wall 2 |  | 3.08 | 4.43 |  | 13.6444 | sqm
| Wall 3 |  | 3.08 | 4.43 |  | 13.6444 | sqm
Physiotherapy Chamber (A10)
| Wall 1 |  | 2.7 | 4.56 |  | 12.312 | sqm
| Wall 2 |  | 2.62 | 3.98 |  | 10.4276 | sqm
| Wall 3 |  | 2.7 | 3.98 |  | 10.746 | sqm
| Wall 4 |  | 2.62 | 3.98 |  | 10.4276 | sqm
Waiting Room (A2)
| Wall 1 |  | 2.79 | 3.98 |  | 11.1042 | sqm
| Wall 2 |  | 4.22 | 3.98 |  | 16.7956 | sqm
| Wall 3 |  | 2.79 | 3.98 |  | 11.1042 | sqm
| Wall 4 |  | 4.22 | 3.98 |  | 16.7956 | sqm
RMO's Chamber (A3)
| Wall 1 |  | 2.78 | 3.98 |  | 11.0644 | sqm
| Wall 2 |  | 4.22 | 3.98 |  | 16.7956 | sqm
| Wall 3 |  | 2.78 | 3.98 |  | 11.0644 | sqm
| Wall 4 |  | 4.22 | 3.98 |  | 16.7956 | sqm
Minor OT (A9)
| Wall 1 |  | 2.78 | 4.56 |  | 12.6768 | sqm
| Wall 2 |  | 2.86 | 3.98 |  | 11.3828 | sqm
| Wall 3 |  | 2.78 | 3.98 |  | 11.0644 | sqm
| Wall 4 |  | 2.86 | 3.98 |  | 11.3828 | sqm
X-Ray room (A4)
| Wall 1 |  | 2.21 | 3 |  | 6.63 | sqm
| Wall 2 |  | 3.24 | 3 |  | 9.72 | sqm
| Wall 3 |  | 3.3 | 3 |  | 9.9 | sqm
| Wall 4 |  | 3.22 | 3 |  | 9.66 | sqm
| Wall 5 |  | 3.02 | 3 |  | 9.06 | sqm
Test Lab (A5)
| Wall 1 |  | 3.3 | 3 |  | 9.9 | sqm
| Wall 2 |  | 4.54 | 3 |  | 13.62 | sqm
| Wall 3 |  | 3.3 | 3 |  | 9.9 | sqm
Dispensary (A6)
| Wall 1 |  | 4.5 | 3 |  | 13.5 | sqm
| Wall 2 |  | 3.19 | 3 |  | 9.57 | sqm
| Wall 3 |  | 4.5 | 3 |  | 13.5 | sqm
| Wall 4 |  | 3.19 | 3 |  | 9.57 | sqm
Medical Store (A7)
| Wall 1 |  | 4.37 | 3 |  | 13.11 | sqm
| Wall 2 |  | 3.1 | 3 |  | 9.3 | sqm
| Wall 3 |  | 4.37 | 3 |  | 13.11 | sqm
Toilet (A18)
| Wall 1 |  | 2.01 | 4.43 |  | 8.9043 | sqm
| Wall 2 |  | 1.01 | 4.43 |  | 4.4743 | sqm
| Wall 3 |  | 2.01 | 4.43 |  | 8.9043 | sqm
| Wall 4 |  | 1.01 | 4.43 |  | 4.4743 | sqm
Toilet (A25)
| Wall 1 |  | 2.76 | 2.72 |  | 7.5072 | sqm
| Wall 2 |  | 2.96 | 3.41 |  | 10.0936 | sqm
| Wall 3 |  | 2.76 | 4.56 |  | 12.5856 | sqm
| Wall 4 |  | 2.96 | 3.41 |  | 10.0936 | sqm
Toilet (A28.1)
| Wall 1 |  | 1.28 | 2.72 |  | 3.4816 | sqm
| Wall 2 |  | 2.92 | 3.41 |  | 9.9572 | sqm
| Wall 3 |  | 1.28 | 4.56 |  | 5.8368 | sqm
sqm
Toilet (A35)
| Wall 1 |  | 2.75 | 2.72 |  | 7.48 | sqm
| Wall 2 |  | 2.65 | 3.41 |  | 9.0365 | sqm
| Wall 3 |  | 2.75 | 4.56 |  | 12.54 | sqm
| Wall 4 |  | 2.65 | 3.41 |  | 9.0365 | sqm
Toilet (A38)
| Wall 1 |  | 1.16 | 4.56 |  | 5.2896 | sqm
| Wall 2 |  | 2.99 | 4.43 |  | 13.2457 | sqm
| Wall 3 |  | 1.16 | 3.61 |  | 4.1876 | sqm
| Wall 4 |  | 2.99 | 4.43 |  | 13.2457 | sqm
Toilet (B9)
| Wall 1 |  | 1.47 | 4.56 |  | 6.7032 | sqm
| Wall 2 |  | 2.51 | 4.43 |  | 11.1193 | sqm
| Wall 3 |  | 1.47 | 3.61 |  | 5.3067 | sqm
| Wall 4 |  | 2.51 | 4.43 |  | 11.1193 | sqm
Toilet (A7.1)
| Wall 1 |  | 1.5 | 3 |  | 4.5 | sqm
| Wall 2 |  | 3.1 | 3 |  | 9.3 | sqm
| Wall 3 |  | 1.5 | 3 |  | 4.5 | sqm
Toilet (A30.1)
| Wall 1 |  | 2.52 | 2.72 |  | 6.8544 | sqm
| Wall 2 |  | 1.58 | 2.72 |  | 4.2976 | sqm
| Wall 3 |  | 1.77 | 2.72 |  | 4.8144 | sqm
| Wall 4 |  | 1.58 | 2.72 |  | 4.2976 | sqm
Bath (32)
| Wall 1 |  | 2.64 | 4.56 |  | 12.0384 | sqm
| Wall 2 |  | 2.88 | 4.56 |  | 13.1328 | sqm
| Wall 3 |  | 2.64 | 4.56 |  | 12.0384 | sqm
| Wall 4 |  | 2.88 | 4.56 |  | 13.1328 | sqm
Bath (24.1)
| Wall 1 |  | 1.84 | 4.56 |  | 8.3904 | sqm
| Wall 2 |  | 2.71 | 4.56 |  | 12.3576 | sqm
| Wall 3 |  | 1.84 | 4.56 |  | 8.3904 | sqm
| Total a |  |  |  |  | 1785.6465 | sqm
Deduction
Boys Ward (A30)
| Door 1 | 3 | 1.44 | 2.4 |  | 10.368 | sqm
| Door 2 | 1 | 1.37 | 2.4 |  | 3.288 | sqm
| Door 3 | 2 | 1.56 | 2.4 |  | 7.488 | sqm
| Door 4 | 1 | 1.275 | 2.4 |  | 3.06 | sqm
| Door 5 | 1 | 0.8 | 2.4 |  | 1.92 | sqm
| Window 1 | 1 | 1.62 | 1.61 |  | 2.6082 | sqm
| Niche | 1 | 1.46 | 1.61 |  | 2.3506 | sqm
| Fanlight | 10 | 1.72 | 0.75 |  | 12.9 | sqm
Lobby (A21)
| Door 1 | 2 | 1.17 | 2.4 |  | 5.616 | sqm
| Door 2 | 2 | 1.34 | 2.4 |  | 6.432 | sqm
| Door 3 | 2 | 1.41 | 2.4 |  | 6.768 | sqm
| Fanlight | 6 | 1.72 | 0.75 |  | 7.74 | sqm
Girls Ward (A22)
| Door 1 | 2 | 1.44 | 2.4 |  | 6.912 | sqm
| Door 2 | 1 | 1.54 | 2.4 |  | 3.696 | sqm
| Door 3 | 1 | 1.34 | 2.4 |  | 3.216 | sqm
| Door 4 | 1 | 1.21 | 2.4 |  | 2.904 | sqm
| Door 5 | 1 | 0.83 | 2.4 |  | 1.992 | sqm
| Door 6 | 1 | 1.25 | 2.4 |  | 3 | sqm
| Window 1 | 1 | 1.63 | 1.61 |  | 2.6243 | sqm
| Niche | 2 | 1.45 | 1.61 |  | 4.669 | sqm
| Fanlight | 6 | 1.75 | 0.75 |  | 7.875 | sqm
Isolation Ward (A32,33,34)
| Door 1 | 1 | 0.76 | 2.1 |  | 1.596 | sqm
| Door 2 | 2 | 1.15 | 2.4 |  | 5.52 | sqm
| Door 3 | 1 | 0.88 | 2.1 |  | 1.848 | sqm
| Door 4 | 1 | 0.71 | 2.1 |  | 1.491 | sqm
| Door 5 | 1 | 1.875 | 2.28 |  | 4.275 | sqm
| Window 1 | 1 | 0.66 | 0.6 |  | 0.396 | sqm
| Window 2 | 1 | 1.19 | 1.38 |  | 1.6422 | sqm
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
Store (A31)
| Door 1 | 1 | 1.275 | 2.4 |  | 3.06 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Staff Ward (A37)
| Door 1 | 1 | 1.22 | 2.4 |  | 2.928 | sqm
| Window 1 | 1 | 1.2 | 1.5 |  | 1.8 | sqm
| Window 2 | 1 | 1.09 | 1.5 |  | 1.635 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Female Isolation Ward (A26,27,28)
| Door 1 | 1 | 1.84 | 2.4 |  | 4.416 | sqm
| Door 2 | 1 | 1.18 | 2.4 |  | 2.832 | sqm
| Door 3 | 1 | 0.83 | 2.4 |  | 1.992 | sqm
| Door 4 | 1 | 0.68 | 2.4 |  | 1.632 | sqm
| Window 1 | 2 | 1.15 | 1.4 |  | 3.22 | sqm
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
Store (A29)
| Door 1 | 1 | 1.25 | 2.4 |  | 3 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Female Staff Ward (A23)
| Door 1 | 1 | 1.34 | 2.4 |  | 3.216 | sqm
| Door 2 | 1 | 1.38 | 2.4 |  | 3.312 | sqm
| Window 1 | 1 | 1.94 | 1.5 |  | 2.91 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
OPD (A11)
| Door 1 | 1 | 2.62 | 2.4 |  | 6.288 | sqm
Observation Room (A13)
| Door 1 | 1 | 1.43 | 2.4 |  | 3.432 | sqm
| Window 1 | 1 | 1.29 | 1.61 |  | 2.0769 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Duty Room (A14)
| Door 1 | 1 | 1.43 | 2.4 |  | 3.432 | sqm
| Door 2 | 1 | 1.67 | 2.4 |  | 4.008 | sqm
| Door 3 | 1 | 0.85 | 2.4 |  | 2.04 | sqm
| Door 4 | 1 | 1.22 | 2.4 |  | 2.928 | sqm
| Window 1 | 2 | 1.4 | 1.38 |  | 3.864 | sqm
| Fanlight | 3 | 1.75 | 0.75 |  | 3.9375 | sqm
Store (A16)
| Window 1 | 2 | 1.4 | 1.38 |  | 3.864 | sqm
| Door 1 | 1 | 0.78 | 2.1 |  | 1.638 | sqm
Foyer (A19)
| Window 1 | 2 | 1.775 | 1.38 |  | 4.899 | sqm
| Door 1 | 1 | 0.82 | 2.1 |  | 1.722 | sqm
Emergency room (A15)
| Window 1 | 1 | 0.82 | 1.38 |  | 1.1316 | sqm
| Door 1 | 1 | 1.165 | 2.1 |  | 2.4465 | sqm
Emergency room (A17)
| Door 1 | 1 | 1.01 | 2.1 |  | 2.121 | sqm
| Door 2 | 1 | 0.99 | 2.4 |  | 2.376 | sqm
Dining Hall (A20)
| Door 1 | 1 | 1.22 | 2.4 |  | 2.928 | sqm
| Door 2 | 1 | 0.74 | 2.4 |  | 1.776 | sqm
| Window 1 | 1 | 1.25 | 1.61 |  | 2.0125 | sqm
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
Physiotherapy Chamber (A10)
| Door 1 | 1 | 1.38 | 2.4 |  | 3.312 | sqm
| Door 2 | 1 | 2.7 | 2.4 |  | 6.48 | sqm
| Door 3 | 1 | 2.62 | 2.4 |  | 6.288 | sqm
Waiting Room (A2)
| Door 1 | 1 | 2.7 | 2.4 |  | 6.48 | sqm
| Door 2 | 1 | 1.33 | 2.4 |  | 3.192 | sqm
| Door 3 | 1 | 1.43 | 2.4 |  | 3.432 | sqm
| Window 1 | 1 | 1.18 | 1.38 |  | 1.6284 | sqm
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
RMO's Chamber (A3)
| Door 1 | 1 | 1.14 | 2.4 |  | 2.736 | sqm
| Door 2 | 1 | 1.17 | 2.4 |  | 2.808 | sqm
| Door 3 | 1 | 1.42 | 2.4 |  | 3.408 | sqm
| Window 1 | 1 | 1.39 | 1.38 |  | 1.9182 | sqm
| Fanlight | 3 | 1.75 | 0.75 |  | 3.9375 | sqm
Minor OT (A9)
| Door 1 | 1 | 1.41 | 2.4 |  | 3.384 | sqm
| Door 2 | 1 | 0.94 | 2.4 |  | 2.256 | sqm
| Window 1 | 1 | 1.595 | 1.61 |  | 2.568 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
X-Ray room (A4)
| Door 1 | 1 | 1.12 | 2.1 |  | 2.352 | sqm
| Door 2 | 1 | 1.32 | 2.1 |  | 2.772 | sqm
| Door 3 | 1 | 1.18 | 2.1 |  | 2.478 | sqm
| Window 1 | 1 | 1.42 | 1.56 |  | 2.2152 | sqm
| Window 2 | 1 | 3.235 | 1.56 |  | 5.0466 | sqm
Test Lab (A5)
| Door 1 | 3 | 1.18 | 2.1 |  | 7.434 | sqm
Dispensary (A6)
| Door 1 | 1 | 1.18 | 1.89 |  | 2.2302 | sqm
| Window 1 | 2 | 1.2 | 1.28 |  | 3.072 | sqm
| Window 2 | 1 | 1.16 | 1.28 |  | 1.4848 | sqm
Medical Store (A7)
| Door 1 | 1 | 1.18 | 1.89 |  | 2.2302 | sqm
| Window 1 | 2 | 0.81 | 1.28 |  | 2.0736 | sqm
| Window 2 | 1 | 1.16 | 1.28 |  | 1.4848 | sqm
Toilet (A18)
| Door 1 | 1 | 0.78 | 2.1 |  | 1.638 | sqm
Toilet (A25)
| Door 1 | 1 | 0.68 | 1.89 |  | 1.2852 | sqm
| Window 1 | 1 | 1.09 | 0.89 |  | 0.9701 | sqm
Toilet (A28.1)
| Window 1 | 1 | 1.28 | 1.18 |  | 1.5104 | sqm
Toilet (A35)
| Door 1 | 1 | 0.71 | 2.1 |  | 1.491 | sqm
| Door 2 | 1 | 0.9 | 2.1 |  | 1.89 | sqm
| Window 1 | 1 | 1.06 | 1.18 |  | 1.2508 | sqm
Toilet (A38)
| Door 1 | 1 | 0.745 | 2.4 |  | 1.788 | sqm
Toilet (B9)
| Door 1 | 1 | 0.77 | 2.4 |  | 1.848 | sqm
| Window 1 | 1 | 1.375 | 1.18 |  | 1.6225 | sqm
Toilet (A7.1)
| Window 1 | 1 | 1.375 | 1.526 |  | 2.0983 | sqm
Bath (32)
| Door 1 | 1 | 1.1 | 2.4 |  | 2.64 | sqm
| Window 1 | 2 | 0.67 | 0.6 |  | 0.804 | sqm
Bath (24.1)
| Door 1 | 1 | 1.21 | 2.4 |  | 2.904 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
| Total b |  |  |  |  | 351.1985 | sqm
| Total (a-b) |  |  |  |  | 1434.448 | sqm
| At different location as per structure demand |  |  |  |  | 15.55 | sqm
| Total |  |  |  |  | 1449.998 | sqm
A7 | Careful removal of existing wooden false ceiling, including all supporting framework, battens, and fixtures, ensuring minimum damage to adjoining surfaces; stacking of all serviceable material at designated location within site premises as directed by the Engineer-in-Charge.
| Area 1 |  |  |  |  | 332.947 | sqm
| Area 2 |  |  |  |  | 420.898 | sqm
| At different location as per structure demand |  |  |  |  | 26.15 | sqm
| Total |  |  |  |  | 779.995 | sqm
| At different location as per structure demand |  |  |  |  | 1 | Job
B. Masonry and Flooring & Wood Work
B1 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources)
| Boys Ward (A30) |  | 12.19 | 6.09 | 0.1 | 7.4237 | cum
| Lobby (A21) |  | 2.355 | 6.09 | 0.1 | 1.4342 | cum
| Girls Ward (A22) |  | 11.92 | 6.09 | 0.1 | 7.2593 | cum
| Isolation Ward (A32,33,34) |  | 8.59 | 2.92 | 0.1 | 2.5083 | cum
| Store (A31) |  | 1.815 | 2.63 | 0.1 | 0.47734 | cum
| Staff Ward (A37) |  | 2.64 | 3.84 | 0.1 | 1.0138 | cum
| Female Isolation Ward (A26,27,28) |  | 7.4 | 2.96 | 0.1 | 2.1904 | cum
| Store (A29) |  | 3.2 | 1.5 | 0.1 | 0.48 | cum
| Female Staff Ward (A23) |  | 2.8 | 4.1 | 0.1 | 1.148 | cum
| OPD (A11) |  | 2.8 | 3.1 | 0.1 | 0.868 | cum
| Consultation Room (A12) |  | 3.9 | 3.1 | 0.1 | 1.209 | cum
| Observation Room (A13) |  | 4.155 | 3.1 | 0.1 | 1.2881 | cum
| Duty Room (A14) |  | 4.2 | 5.6 | 0.1 | 2.352 | cum
| Store (A16) |  | 2.09 | 1.4 | 0.1 | 0.2926 | cum
| Emergency room (A15) |  | 2.03 | 1.445 | 0.1 | 0.29334 | cum
| Emergency room (A17) |  | 2.71 | 2.03 | 0.1 | 0.55013 | cum
| Foyer (A19) |  | 1.775 | 1.28 | 0.1 | 0.2272 | cum
| Dining Hall (A20) |  | 10.94 | 2.99 | 0.1 | 3.2711 | cum
| Physiotherapy Chamber (A10) |  | 2.7 | 2.62 | 0.1 | 0.7074 | cum
| Minor OT (A9) |  | 2.78 | 2.86 | 0.1 | 0.79508 | cum
| Waiting Room (A2) |  | 2.79 | 4.22 | 0.1 | 1.1774 | cum
| RMO's Chamber (A3) |  | 2.78 | 4.22 | 0.1 | 1.1732 | cum
| Office Reception (A1) |  | 2.895 | 1.56 | 0.1 | 0.45162 | cum
| Office Reception (A1) |  | 2.895 | 0.5 | 0.45 | 0.65138 | cum
| X-Ray room (A4) |  | 5.2 | 3.3 | 0.1 | 1.716 | cum
| Test Lab (A5) |  | 4.54 | 3.3 | 0.1 | 1.4982 | cum
| Dispensary (A6) |  | 4.5 | 3.19 | 0.1 | 1.4355 | cum
| Medical Store (A7) |  | 4.37 | 3.1 | 0.1 | 1.3547 | cum
| Toilet (A18) |  | 1.005 | 2.01 | 0.1 | 0.202 | cum
| Toilet (A25) |  | 2.76 | 2.96 | 0.1 | 0.81696 | cum
| Toilet (A28.1) |  | 1.28 | 2.92 | 0.1 | 0.37376 | cum
| Toilet (A35) |  | 2.75 | 2.65 | 0.1 | 0.72875 | cum
| Toilet (A38) |  | 1.16 | 2.99 | 0.1 | 0.34684 | cum
| Toilet (B9) |  | 1.47 | 2.51 | 0.1 | 0.36897 | cum
| Toilet (A7.1) |  | 1.5 | 3.1 | 0.1 | 0.465 | cum
| Toilet (A23.1) |  | 3 | 1.7 | 0.1 | 0.51 | cum
| Toilet (A30.1) |  | 2.52 | 1.58 | 0.1 | 0.39816 | cum
| Bath (A32) |  | 2.64 | 2.885 | 0.1 | 0.76164 | cum
| Bath (A32.2) |  | 1.5 | 1 | 0.1 | 0.15 | cum
| Bath (24.1) |  | 1.835 | 2.71 | 0.1 | 0.49729 | cum
| Total |  |  |  |  | 50.8661 | cum
| 20% of total quantity to be taken |  |  |  |  | 10.1732 | cum
| At different location as per structure demand |  |  |  |  | 1.83 | cum
| Total |  |  |  |  | 12.0032 | cum
B2 | 40 mm thick fine dressed stone flooring over 20 mm (average) thick base of cement mortar 1:5 (1 cement : 5 coarse sand) with joints finished flush. White sand stone
| Garage Area |  |  |  |  | 26.3 | sqm
| At different location as per structure demand |  |  |  |  | 3.7 | sqm
| Total |  |  |  |  | 30 | sqm
B3 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:4 (1 cement : 4 coarse sand)
Hospital Area
| 1 | 1 | 3.1 | 0.23 | 3.13 | 2.2317 | cum
| 2 | 3 | 1.18 | 0.5 | 2.02 | 3.5754 | cum
| 3 | 1 | 4.54 | 0.4 | 3.13 | 5.6841 | cum
| 4 | 1 | 3.24 | 0.4 | 1.52 | 1.9699 | cum
| 5 | 2 | 1.65 | 0.09 | 2.35 | 0.69795 | cum
| 6 | 1 | 2.91 | 0.09 | 2.49 | 0.65213 | cum
| 7 | 1 | 0.94 | 0.765 | 2.4 | 1.7258 | cum
| 8 | 1 | 2.02 | 0.2 | 2.68 | 1.0827 | cum
| 9 | 1 | 2.62 | 0.51 | 2.4 | 3.2069 | cum
| 10 | 1 | 1.38 | 0.69 | 2.4 | 2.2853 | cum
| 11 | 1 | 0.76 | 0.23 | 2.1 | 0.36708 | cum
| 12 | 1 | 2.71 | 0.12 | 3.33 | 1.0829 | cum
| 13 | 1 | 1.84 | 0.12 | 3.33 | 0.73526 | cum
| 14 | 1 | 0.68 | 0.5 | 2.1 | 0.714 | cum
| 15 | 1 | 0.83 | 0.66 | 2.4 | 1.3147 | cum
| 16 | 1 | 2.92 | 0.12 | 3.41 | 1.1949 | cum
| 17 | 4 | 1.55 | 0.52 | 1.61 | 5.1906 | cum
| 18 | 1 | 1.29 | 0.69 | 1.6 | 1.4242 | cum
| 19 | 2 | 3.08 | 0.12 | 3.41 | 2.5207 | cum
| 20 | 1 | 11.39 | 0.3 | 2.86 | 9.7726 | cum
| 21 | 1 | 0.78 | 0.5 | 2.1 | 0.819 | cum
| 22 | 1 | 1.14 | 0.5 | 2.4 | 1.368 | cum
| 23 | 1 | 10.85 | 0.3 | 2.86 | 9.3093 | cum
| 24 | 1 | 1.2 | 0.66 | 2.4 | 1.9008 | cum
| 25 | 1 | 0.8 | 0.66 | 4.53 | 2.3918 | cum
| 26 | 1 | 1.82 | 0.23 | 3.41 | 1.4274 | cum
| 27 | 1 | 0.705 | 0.49 | 2.4 | 0.82908 | cum
| 28 | 1 | 0.9 | 0.5 | 2.4 | 1.08 | cum
| 29 | 1 | 2.64 | 0.12 | 3.38 | 1.0708 | cum
| 30 | 1 | 1.5 | 0.12 | 3.38 | 0.6084 | cum
| 31 | 1 | 2.48 | 0.12 | 3.38 | 1.0059 | cum
| 32 | 1 | 1.38 | 0.48 | 1.41 | 0.93398 | cum
| 33 | 1 | 1.27 | 0.48 | 2.4 | 1.463 | cum
| 34 | 1 | 0.75 | 0.52 | 2.4 | 0.936 | cum
| TOTAL a |  |  |  |  | 72.5724 | cum
Deduction
| Door 1 | 1 | 0.89 | 0.2 | 2.1 | 0.3738 | cum
| Door 2 | 1 | 1.9 | 0.09 | 1.92 | 0.32832 | cum
| Door 3 | 1 | 0.89 | 0.2 | 2.1 | 0.3738 | cum
| Door 4 | 1 | 0.85 | 0.12 | 2.1 | 0.2142 | cum
| Window 1 | 1 | 11.39 | 0.3 | 1.63 | 5.5697 | cum
| Window 2 | 1 | 10.85 | 0.3 | 1.63 | 5.3056 | cum
| Window 3 | 2 | 0.9 | 0.09 | 1.12 | 0.18144 | cum
| TOTAL b |  |  |  |  | 12.3469 | cum
| TOTAL (a-b) |  |  |  |  | 60.2254 | cum
| At different location as per structure demand |  |  |  |  | 1.77 | cum
| Total |  |  |  |  | 61.9954 | cum
B4 | 12 mm cement plaster finished with a floating coat of neat cement of mix : 1:4 (1 cement: 4 fine sand)
Boys Ward (A30)
| Wall 1 |  | 12.19 | 2.16 |  | 26.3304 | sqm
| Wall 2 |  | 6.09 | 3.55 |  | 21.6195 | sqm
| Wall 3 |  | 12.19 | 2.16 |  | 26.3304 | sqm
| Wall 4 |  | 6.09 | 3.55 |  | 21.6195 | sqm
Lobby (A21)
| Wall 1 |  | 2.355 | 4.56 |  | 10.7388 | sqm
| Wall 2 |  | 6.09 | 5.95 |  | 36.2355 | sqm
| Wall 3 |  | 2.39 | 4.56 |  | 10.8984 | sqm
| Wall 4 |  | 6.09 | 5.95 |  | 36.2355 | sqm
Girls Ward (A22)
| Wall 1 |  | 11.915 | 2.16 |  | 25.7364 | sqm
| Wall 2 |  | 6.09 | 3.55 |  | 21.6195 | sqm
| Wall 3 |  | 11.92 | 2.16 |  | 25.7472 | sqm
| Wall 4 |  | 6.09 | 3.55 |  | 21.6195 | sqm
Isolation Ward (A32,33,34)
| Wall 1 |  | 8.59 | 2.16 |  | 18.5544 | sqm
| Wall 2 |  | 2.92 | 1.01 |  | 2.9492 | sqm
| Wall 3 |  | 8.59 | 2.16 |  | 18.5544 | sqm
| Wall 4 |  | 1.04 | 1.01 |  | 1.0504 | sqm
Store (A31)
| Wall 1 |  | 2.63 | 4.56 |  | 11.9928 | sqm
| Wall 2 |  | 1.82 | 3.41 |  | 6.2062 | sqm
| Wall 3 |  | 2.63 | 4.56 |  | 11.9928 | sqm
| Wall 2 |  | 1.82 | 3.41 |  | 6.2062 | sqm
Staff Ward (A37)
| Wall 1 |  | 2.64 | 2.16 |  | 5.7024 | sqm
| Wall 2 |  | 3.84 | 3.55 |  | 13.632 | sqm
| Wall 3 |  | 2.64 | 3.55 |  | 9.372 | sqm
| Wall 4 |  | 3.84 | 3.55 |  | 13.632 | sqm
Female Isolation Ward (A26,27,28)
| Wall 1 |  | 7.51 | 0.32 |  | 2.4032 | sqm
| Wall 2 |  | 2.96 | 1.01 |  | 2.9896 | sqm
| Wall 3 |  | 7.51 | 2.16 |  | 16.2216 | sqm
| Wall 4 |  | 2.96 | 1.01 |  | 2.9896 | sqm
Store (A29)
| Wall 1 |  | 2.91 | 4.56 |  | 13.2696 | sqm
| Wall 2 |  | 1.59 | 3.41 |  | 5.4219 | sqm
| Wall 3 |  | 3.27 | 3.41 |  | 11.1507 | sqm
| Wall 4 |  | 1.59 | 3.41 |  | 5.4219 | sqm
Female Staff Ward (A23)
| Wall 1 |  | 2.71 | 2.16 |  | 5.8536 | sqm
| Wall 2 |  | 4.14 | 3.55 |  | 14.697 | sqm
| Wall 3 |  | 2.71 | 2.16 |  | 5.8536 | sqm
| Wall 4 |  | 4.14 | 3.55 |  | 14.697 | sqm
OPD (A11)
| Wall 1 |  | 4.16 | 4.56 |  | 18.9696 | sqm
| Wall 2 |  | 3.08 | 3.37 |  | 10.3796 | sqm
| Wall 3 |  | 4.16 | 2.85 |  | 11.856 | sqm
| Wall 4 |  | 3.08 | 3.37 |  | 10.3796 | sqm
Consultation Room (A12)
| Wall 1 |  | 2.85 | 4.56 |  | 12.996 | sqm
| Wall 2 |  | 3.08 | 3.37 |  | 10.3796 | sqm
| Wall 3 |  | 2.85 | 2.85 |  | 8.1225 | sqm
| Wall 4 |  | 3.08 | 3.37 |  | 10.3796 | sqm
Observation Room (A13)
| Wall 1 |  | 4.15 | 4.56 |  | 18.924 | sqm
| Wall 2 |  | 3.08 | 3.37 |  | 10.3796 | sqm
| Wall 3 |  | 4.15 | 2.85 |  | 11.8275 | sqm
| Wall 4 |  | 3.08 | 3.37 |  | 10.3796 | sqm
Duty Room (A14)
| Wall 1 |  | 4.27 | 4.56 |  | 19.4712 | sqm
| Wall 2 |  | 5.63 | 3.37 |  | 18.9731 | sqm
| Wall 3 |  | 4.27 | 4.43 |  | 18.9161 | sqm
| Wall 4 |  | 5.63 | 3.37 |  | 18.9731 | sqm
Store (A16)
| Wall 1 |  | 1.92 | 4.43 |  | 8.5056 | sqm
| Wall 2 |  | 1.38 | 4.43 |  | 6.1134 | sqm
| Wall 3 |  | 1.25 | 4.43 |  | 5.5375 | sqm
| Wall 4 |  | 0.52 | 4.43 |  | 2.3036 | sqm
Foyer (A19)
| Wall 1 |  | 1.78 | 4.43 |  | 7.8854 | sqm
| Wall 2 |  | 1.28 | 4.43 |  | 5.6704 | sqm
| Wall 3 |  | 1.78 | 4.43 |  | 7.8854 | sqm
| Wall 4 |  | 1.28 | 4.43 |  | 5.6704 | sqm
Emergency room (A15)
| Wall 1 |  | 2.03 | 4.43 |  | 8.9929 | sqm
| Wall 2 |  | 1.44 | 4.43 |  | 6.3792 | sqm
| Wall 3 |  | 1.44 | 4.43 |  | 6.3792 | sqm
Emergency room (A17)
| Wall 1 |  | 2.03 | 4.43 |  | 8.9929 | sqm
| Wall 2 |  | 2.71 | 4.43 |  | 12.0053 | sqm
| Wall 3 |  | 2.71 | 4.43 |  | 12.0053 | sqm
Dining Hall (A20)
| Wall 1 |  | 10.94 | 4.56 |  | 49.8864 | sqm
| Wall 2 |  | 3.08 | 3.37 |  | 10.3796 | sqm
| Wall 3 |  | 10.94 | 2.85 |  | 31.179 | sqm
| Wall 4 |  | 3.08 | 3.37 |  | 10.3796 | sqm
Physiotherapy Chamber (A10)
| Wall 1 |  | 2.7 | 4.56 |  | 12.312 | sqm
| Wall 2 |  | 2.62 | 3.98 |  | 10.4276 | sqm
| Wall 3 |  | 2.7 | 3.98 |  | 10.746 | sqm
| Wall 4 |  | 2.62 | 3.98 |  | 10.4276 | sqm
Waiting Room (A2)
| Wall 1 |  | 2.79 | 3.98 |  | 11.1042 | sqm
| Wall 2 |  | 4.22 | 3.98 |  | 16.7956 | sqm
| Wall 3 |  | 2.79 | 3.98 |  | 11.1042 | sqm
| Wall 4 |  | 4.22 | 3.98 |  | 16.7956 | sqm
RMO's Chamber (A3)
| Wall 1 |  | 2.78 | 3.98 |  | 11.0644 | sqm
| Wall 2 |  | 4.22 | 3.98 |  | 16.7956 | sqm
| Wall 3 |  | 2.78 | 3.98 |  | 11.0644 | sqm
| Wall 4 |  | 4.22 | 3.98 |  | 16.7956 | sqm
Minor OT (A9)
| Wall 1 |  | 2.78 | 4.56 |  | 12.6768 | sqm
| Wall 2 |  | 2.86 | 3.98 |  | 11.3828 | sqm
| Wall 3 |  | 2.78 | 3.98 |  | 11.0644 | sqm
| Wall 4 |  | 2.86 | 3.98 |  | 11.3828 | sqm
X-Ray room (A4)
| Wall 1 |  | 2.21 | 3 |  | 6.63 | sqm
| Wall 2 |  | 3.24 | 3 |  | 9.72 | sqm
| Wall 3 |  | 3.3 | 3 |  | 9.9 | sqm
| Wall 4 |  | 3.22 | 3 |  | 9.66 | sqm
| Wall 5 |  | 3.02 | 3 |  | 9.06 | sqm
Test Lab (A5)
| Wall 1 |  | 3.3 | 3 |  | 9.9 | sqm
| Wall 2 |  | 4.54 | 3 |  | 13.62 | sqm
| Wall 3 |  | 3.3 | 3 |  | 9.9 | sqm
| Wall 4 |  | 4.54 | 3 |  | 13.62 | sqm
Dispensary (A6)
| Wall 1 |  | 4.5 | 3 |  | 13.5 | sqm
| Wall 2 |  | 3.19 | 3 |  | 9.57 | sqm
| Wall 3 |  | 4.5 | 3 |  | 13.5 | sqm
| Wall 4 |  | 3.19 | 3 |  | 9.57 | sqm
Medical Store (A7)
| Wall 1 |  | 4.37 | 3 |  | 13.11 | sqm
| Wall 2 |  | 3.1 | 3 |  | 9.3 | sqm
| Wall 3 |  | 4.37 | 3 |  | 13.11 | sqm
| Wall 4 |  | 3.1 | 3 |  | 9.3 | sqm
(A24)
| Wall 1 |  | 1.84 | 4.035 |  | 7.4244 | sqm
| Wall 2 |  | 1.095 | 4.035 |  | 4.4183 | sqm
| Wall 3 |  | 1.84 | 4.035 |  | 7.4244 | sqm
| Wall 4 |  | 1.095 | 4.035 |  | 4.4183 | sqm
(A32)
| Wall 1 |  | 2.48 | 4.56 |  | 11.3088 | sqm
| Wall 2 |  | 1.02 | 2.86 |  | 2.9172 | sqm
| Wall 3 |  | 2.48 | 2.86 |  | 7.0928 | sqm
| Wall 4 |  | 1.02 | 2.86 |  | 2.9172 | sqm
Toilet (A18)
| Wall 1 |  | 2.01 | 2.13 |  | 4.2813 | sqm
| Wall 2 |  | 1.01 | 2.13 |  | 2.1513 | sqm
| Wall 3 |  | 2.01 | 2.13 |  | 4.2813 | sqm
| Wall 4 |  | 1.01 | 2.13 |  | 2.1513 | sqm
Toilet (A25)
| Wall 1 |  | 2.76 | 0.42 |  | 1.1592 | sqm
| Wall 2 |  | 2.96 | 1.11 |  | 3.2856 | sqm
| Wall 3 |  | 2.76 | 2.26 |  | 6.2376 | sqm
| Wall 4 |  | 2.96 | 1.11 |  | 3.2856 | sqm
Toilet (A28.1)
| Wall 1 |  | 1.28 | 0.42 |  | 0.5376 | sqm
| Wall 2 |  | 2.92 | 1.11 |  | 3.2412 | sqm
| Wall 3 |  | 1.28 | 2.26 |  | 2.8928 | sqm
| Wall 4 |  | 2.92 | 1.11 |  | 3.2412 | sqm
Toilet (A35)
| Wall 1 |  | 2.75 | 0.42 |  | 1.155 | sqm
| Wall 2 |  | 2.65 | 1.11 |  | 2.9415 | sqm
| Wall 3 |  | 2.75 | 2.26 |  | 6.215 | sqm
| Wall 4 |  | 2.65 | 1.11 |  | 2.9415 | sqm
Toilet (A38)
| Wall 1 |  | 1.16 | 2.26 |  | 2.6216 | sqm
| Wall 2 |  | 2.99 | 2.13 |  | 6.3687 | sqm
| Wall 3 |  | 1.16 | 1.31 |  | 1.5196 | sqm
| Wall 4 |  | 2.99 | 2.13 |  | 6.3687 | sqm
Toilet (B9)
| Wall 1 |  | 1.47 | 2.26 |  | 3.3222 | sqm
| Wall 2 |  | 2.51 | 2.13 |  | 5.3463 | sqm
| Wall 3 |  | 1.47 | 1.31 |  | 1.9257 | sqm
| Wall 4 |  | 2.51 | 2.13 |  | 5.3463 | sqm
Toilet (A7.1)
| Wall 1 |  | 1.5 | 0.7 |  | 1.05 | sqm
| Wall 2 |  | 3.1 | 0.7 |  | 2.17 | sqm
| Wall 3 |  | 1.5 | 0.7 |  | 1.05 | sqm
| Wall 4 |  | 3.1 | 0.7 |  | 2.17 | sqm
Toilet (A30.1)
| Wall 1 |  | 2.52 | 0.42 |  | 1.0584 | sqm
| Wall 2 |  | 1.58 | 0.42 |  | 0.6636 | sqm
| Wall 3 |  | 1.77 | 0.42 |  | 0.7434 | sqm
| Wall 4 |  | 1.58 | 0.42 |  | 0.6636 | sqm
Toilet (A23.1)
| Wall 1 |  | 3 | 0.3 |  | 0.9 | sqm
| Wall 2 |  | 1.84 | 0.3 |  | 0.552 | sqm
| Wall 3 |  | 3 | 0.3 |  | 0.9 | sqm
| Wall 4 |  | 1.84 | 0.3 |  | 0.552 | sqm
Bath (A32.1)
| Wall 1 |  | 1.5 | 0.56 |  | 0.84 | sqm
| Wall 2 |  | 1.32 | 0.56 |  | 0.7392 | sqm
| Wall 3 |  | 1.5 | 0.56 |  | 0.84 | sqm
| Wall 4 |  | 1.32 | 0.56 |  | 0.7392 | sqm
Bath (A32.2)
| Wall 1 |  | 1.5 | 0.56 |  | 0.84 | sqm
| Wall 2 |  | 1 | 0.56 |  | 0.56 | sqm
| Wall 3 |  | 1.5 | 0.56 |  | 0.84 | sqm
| Wall 4 |  | 1 | 0.56 |  | 0.56 | sqm
Bath (24.1)
| Wall 1 |  | 1.84 | 2.26 |  | 4.1584 | sqm
| Wall 2 |  | 2.71 | 2.26 |  | 6.1246 | sqm
| Wall 3 |  | 1.84 | 2.26 |  | 4.1584 | sqm
| Wall 4 |  | 2.71 | 2.26 |  | 6.1246 | sqm
| Total a |  |  |  |  | 1487.649 | sqm
Deductions
Boys Ward (A30)
| Fanlight | 10 | 1.72 | 0.75 |  | 12.9 | sqm
Lobby (A21)
| Door 1 | 2 | 1.17 | 2.4 |  | 5.616 | sqm
| Door 2 | 2 | 1.34 | 2.4 |  | 6.432 | sqm
| Door 3 | 2 | 1.41 | 2.4 |  | 6.768 | sqm
| Fanlight | 6 | 1.72 | 0.75 |  | 7.74 | sqm
Girls Ward (A22)
| Fanlight | 6 | 1.75 | 0.75 |  | 7.875 | sqm
Isolation Ward (A32,33,34)
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
Store (A31)
| Door 1 | 1 | 1.275 | 2.4 |  | 3.06 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Staff Ward (A37)
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Female Isolation Ward (A26,27,28)
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
Store (A29)
| Door 1 | 1 | 1.25 | 2.4 |  | 3 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Female Staff Ward (A23)
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
OPD (A11)
| Door 1 | 1 | 1.11 | 2.61 |  | 2.8971 | sqm
| Window 1 | 1 | 2.75 | 2.61 |  | 7.1775 | sqm
Consultation room (A12)
| Door 1 | 1 | 1 | 2.61 |  | 2.61 | sqm
| Window 1 | 2 | 0.82 | 1.59 |  | 2.6076 | sqm
Observation Room (A13)
| Door 1 | 1 | 1.43 | 2.4 |  | 3.432 | sqm
| Door 2 | 1 | 1.11 | 2.61 |  | 2.8971 | sqm
| Window 1 | 1 | 2.75 | 1.59 |  | 4.3725 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Duty Room (A14)
| Door 1 | 1 | 1.43 | 2.4 |  | 3.432 | sqm
| Door 2 | 1 | 1.67 | 2.4 |  | 4.008 | sqm
| Door 3 | 1 | 0.85 | 2.4 |  | 2.04 | sqm
| Door 4 | 1 | 1.22 | 2.4 |  | 2.928 | sqm
| Window 1 | 2 | 1.4 | 1.38 |  | 3.864 | sqm
| Fanlight | 3 | 1.75 | 0.75 |  | 3.9375 | sqm
Store (A16)
| Window 1 | 2 | 1.4 | 1.38 |  | 3.864 | sqm
| Door 1 | 1 | 0.78 | 2.1 |  | 1.638 | sqm
Foyer (A19)
| Window 1 | 1 | 0.81 | 1.38 |  | 1.1178 | sqm
| Door 1 | 2 | 0.82 | 2.1 |  | 3.444 | sqm
Emergency room (A15)
| Door 1 | 1 | 0.855 | 2.36 |  | 2.0178 | sqm
| Door 2 | 1 | 0.85 | 2.1 |  | 1.785 | sqm
| Door 3 | 1 | 0.99 | 2.1 |  | 2.079 | sqm
| Door 4 | 1 | 1.26 | 2.4 |  | 3.024 | sqm
Emergency room (A17)
| Door 1 | 1 | 0.82 | 2.1 |  | 1.722 | sqm
| Door 3 | 1 | 1.26 | 2.4 |  | 3.024 | sqm
| Window 1 | 1 | 0.82 | 1.38 |  | 1.1316 | sqm
Dining Hall (A20)
| Door 1 | 1 | 1 | 2.61 |  | 2.61 | sqm
| Window 1 | 2 | 0.82 | 1.59 |  | 2.6076 | sqm
| Window 2 | 2 | 0.915 | 1.59 |  | 2.9097 | sqm
| Window 3 | 2 | 2.75 | 1.59 |  | 8.745 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
Physiotherapy Chamber (A10)
| Door 1 | 1 | 1.2 | 2.4 |  | 2.88 | sqm
Waiting Room (A2)
| Door 1 | 1 | 1.2 | 2.4 |  | 2.88 | sqm
| Door 2 | 1 | 1.33 | 2.4 |  | 3.192 | sqm
| Door 3 | 1 | 1.43 | 2.4 |  | 3.432 | sqm
| Window 1 | 1 | 1.18 | 1.38 |  | 1.6284 | sqm
| Fanlight | 2 | 1.75 | 0.75 |  | 2.625 | sqm
RMO's Chamber (A3)
| Door 1 | 1 | 1.14 | 2.4 |  | 2.736 | sqm
| Door 2 | 1 | 1.17 | 2.4 |  | 2.808 | sqm
| Door 3 | 1 | 1.42 | 2.4 |  | 3.408 | sqm
| Window 1 | 1 | 1.39 | 1.38 |  | 1.9182 | sqm
| Fanlight | 3 | 1.75 | 0.75 |  | 3.9375 | sqm
Minor OT (A9)
| Door 1 | 1 | 1.41 | 2.4 |  | 3.384 | sqm
| Window 1 | 1 | 1.595 | 1.61 |  | 2.568 | sqm
| Fanlight | 1 | 1.75 | 0.75 |  | 1.3125 | sqm
X-Ray room (A4)
| Door 1 | 1 | 1.12 | 2.4 |  | 2.688 | sqm
| Door 2 | 1 | 1.32 | 2.12 |  | 2.7984 | sqm
Test Lab (A5)
| Door 1 | 3 | 1.18 | 2.12 |  | 7.5048 | sqm
Dispensary (A6)
| Door 1 | 1 | 1.34 | 2.12 |  | 2.8408 | sqm
| Window 1 | 2 | 1.2 | 1.28 |  | 3.072 | sqm
| Window 2 | 1 | 1.16 | 1.28 |  | 1.4848 | sqm
Medical Store (A7)
| Door 1 | 1 | 1.18 | 1.89 |  | 2.2302 | sqm
| Window 1 | 1 | 0.81 | 1.28 |  | 1.0368 | sqm
| Window 2 | 2 | 1.16 | 1.28 |  | 2.9696 | sqm
| Total b |  |  |  |  | 219.7737 | sqm
| Total (a-b) |  |  |  |  | 1267.8753 | sqm
| At different location as per structure demand |  |  |  |  | 32.12 | sqm
| Total |  |  |  |  | 1299.9953 | sqm
| 50% quantity to be taken |  |  |  |  | 649.9976 | sqm
B5 | Wall painting with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. Two coats
| Total quantity |  |  |  |  | 1500 | sqm
B5 | Random rubble masonry with hard stone in superstructure above plinth level and upto floor five level, including leveling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) at window sills, ceiling level and the like. Cement mortar 1:6 (1 cement : 6 coarse sand)
| For retaining wall |  | 30 | 0.6 | 1.5 | 27 | cum
| At different location as per structure demand |  |  |  |  | 3 | cum
| Total |  |  |  |  | 30 | cum
B6 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : 25 mm thick
| Boys Ward (A30) |  | 12.19 | 6.09 |  | 74.2371 | sqm
| Lobby (A21) |  | 2.355 | 6.09 |  | 14.3419 | sqm
| Girls Ward (A22) |  | 12.19 | 6.09 |  | 74.2371 | sqm
| Isolation Ward (A32,33,34) |  | 8.59 | 2.92 |  | 25.0828 | sqm
| Store (A31) |  | 1.815 | 2.63 |  | 4.7734 | sqm
| Staff Ward (A37) |  | 2.64 | 3.84 |  | 10.1376 | sqm
| Female Isolation Ward (A26,27,28) |  | 7.4 | 2.96 |  | 21.904 | sqm
| Store (A29) |  | 3.2 | 1.5 |  | 4.8 | sqm
| Female Staff Ward (A23) |  | 2.8 | 4.1 |  | 11.48 | sqm
| OPD (A11) |  | 2.8 | 3.1 |  | 8.68 | sqm
| Consultation Room (A12) |  | 3.9 | 3.1 |  | 12.09 | sqm
| Observation Room (A13) |  | 4.155 | 3.1 |  | 12.8805 | sqm
| Duty Room (A14) |  | 4.2 | 5.6 |  | 23.52 | sqm
| Store (A16) |  | 2.09 | 1.4 |  | 2.926 | sqm
| Emergency room (A15) |  | 2.03 | 1.445 |  | 2.9333 | sqm
| Emergency room (A17) |  | 2.71 | 2.03 |  | 5.5013 | sqm
| Foyer (A19) |  | 1.775 | 1.28 |  | 2.272 | sqm
| Dining Hall (A20) |  | 10.94 | 2.99 |  | 32.7106 | sqm
| Physiotherapy Chamber (A10) |  | 2.7 | 2.62 |  | 7.074 | sqm
| Minor OT (A9) |  | 2.78 | 2.86 |  | 7.9508 | sqm
| Waiting Room (A2) |  | 2.79 | 4.22 |  | 11.7738 | sqm
| RMO's Chamber (A3) |  | 2.78 | 4.22 |  | 11.7316 | sqm
| Office Reception (A1) |  | 2.895 | 1.56 |  | 4.5162 | sqm
| X-Ray room (A4) |  | 5.2 | 3.3 |  | 17.16 | sqm
| Test Lab (A5) |  | 4.54 | 3.3 |  | 14.982 | sqm
| Dispensary (A6) |  | 4.5 | 3.19 |  | 14.355 | sqm
| Medical Store (A7) |  | 4.37 | 3.1 |  | 13.547 | sqm
| (A24) |  | 1.1 | 1.84 |  | 2.024 | sqm
| (A32) |  | 1.02 | 2.48 |  | 2.5296 | sqm
RMO's Residence
| Drawing room |  | 6.1 | 4.2 |  | 25.62 | sqm
| Dining Room |  | 3 | 3 |  | 9 | sqm
| Bedroom Room 1 |  | 5.6 | 4.6 |  | 25.76 | sqm
| Dressing |  | 2 | 4.6 |  | 9.2 | sqm
| Bedroom Room 2 |  | 4.6 | 5.4 |  | 24.84 | sqm
| Verandah 1 |  | 4 | 1.8 |  | 7.2 | sqm
| Kitchen |  | 4 | 1.8 |  | 7.2 | sqm
| Verandah 2 |  | 3.3 | 2.9 |  | 9.57 | sqm
Nurse's Residence
| Living Room |  | 4 | 5.6 |  | 22.4 | sqm
| Foyer |  | 3.4 | 2.8 |  | 9.52 | sqm
| Bedroom 1 |  | 2.7 | 6.9 |  | 18.63 | sqm
| Bedroom 2 |  | 2.9 | 4.2 |  | 12.18 | sqm
| Kitchen |  | 2.7 | 2.7 |  | 7.29 | sqm
| At different location as per structure demand |  |  |  |  | 59.44 | sqm
| Total |  |  |  |  | 700.0018 | sqm
B7 | Kota stone slabs 20 mm thick in risers of steps, skirting, dado and pillars laid on 12 mm (average) thick cement mortar 1:3 (1 cement: 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slabs, including rubbing and polishing complete.
| Lobby (A21) |  | 9.13 | 0.15 |  | 1.3695 | sqm
| Store (A31) |  | 7.61 | 0.15 |  | 1.1415 | sqm
| Store (A29) |  | 7.73 | 0.15 |  | 1.1595 | sqm
| OPD (A11) |  | 13.43 | 0.15 |  | 2.0145 | sqm
| Consultation Room (A12) |  | 10.97 | 0.15 |  | 1.6455 | sqm
| Observation Room (A13) |  | 13.42 | 0.15 |  | 2.013 | sqm
| Duty Room (A14) |  | 15.29 | 0.15 |  | 2.2935 | sqm
| Store (A16) |  | 6.4 | 0.15 |  | 0.96 | sqm
| Emergency room (A15) |  | 4.01 | 0.15 |  | 0.6015 | sqm
| Emergency room (A17) |  | 6.55 | 0.15 |  | 0.9825 | sqm
| Foyer (A19) |  | 4 | 0.15 |  | 0.6 | sqm
| Dining Hall (A20) |  | 26.04 | 0.15 |  | 3.906 | sqm
| Physiotherapy Chamber (A10) |  | 9.48 | 0.15 |  | 1.422 | sqm
| Minor OT (A9) |  | 10.61 | 0.15 |  | 1.5915 | sqm
| Waiting Room (A2) |  | 8.75 | 0.15 |  | 1.3125 | sqm
| RMO's Chamber (A3) |  | 9.04 | 0.15 |  | 1.356 | sqm
| Office Reception (A1) |  | 2.895 | 0.15 |  | 0.43425 | sqm
| X-Ray room (A4) |  | 12.56 | 0.15 |  | 1.884 | sqm
| Test Lab (A5) |  | 14.5 | 0.15 |  | 2.175 | sqm
| Dispensary (A6) |  | 14.04 | 0.15 |  | 2.106 | sqm
| Medical Store (A7) |  | 13.78 | 0.15 |  | 2.067 | sqm
| (A24) |  | 3.19 | 0.15 |  | 0.4785 | sqm
| (A32) |  | 3.73 | 0.15 |  | 0.5595 | sqm
RMO's Residence
| Drawing room |  | 6.1 | 0.15 |  | 0.915 | sqm
| Dining Room |  | 3 | 0.15 |  | 0.45 | sqm
| Bedroom Room 1 |  | 5.6 | 0.15 |  | 0.84 | sqm
| Dressing |  | 2 | 0.15 |  | 0.3 | sqm
| Bedroom Room 2 |  | 4.6 | 0.15 |  | 0.69 | sqm
| Verandah 1 |  | 4 | 0.15 |  | 0.6 | sqm
| Kitchen |  | 4 | 0.15 |  | 0.6 | sqm
| Verandah 2 |  | 3.3 | 0.15 |  | 0.495 | sqm
Nurse's Residence
| Living Room |  | 4 | 0.15 |  | 0.6 | sqm
| Foyer |  | 3.4 | 0.15 |  | 0.51 | sqm
| Bedroom 1 |  | 2.7 | 0.15 |  | 0.405 | sqm
| Bedroom 2 |  | 2.9 | 0.15 |  | 0.435 | sqm
| Kitchen |  | 2.7 | 0.15 |  | 0.405 | sqm
| At different location as per structure demand |  |  |  |  | 5.93 | sqm
| Total |  |  |  |  | 47.2482 | sqm
B8 | Providing and laying Ceramic glazed floor tiles of size 300x300 mm(thickness to be specified by the manufacturer) of 1st quality conforming to IS : 15622 of approved make in colours such as White, Ivory, Grey, Fume Red Brown, laid on 20 mm thick cement mortar 1:4 (1 Cement : 4 Coarse sand), Jointing with grey cement slurry @ 3.3 kg/sqm including pointing the joints with white cement and matching pigment etc., complete.
Boys Ward (A30)
| Wall 1 |  | 12.19 | 2.4 |  | 58.59 | sqm
| Wall 2 |  | 6.09 | 2.4 |  | 21.6195 | sqm
| Wall 3 |  | 12.19 | 2.4 |  | 26.3304 | sqm
| Wall 4 |  | 6.09 | 2.4 |  | 21.6195 | sqm
Girls Ward (A22)
| Wall 1 |  | 11.915 | 2.4 |  | 25.7364 | sqm
| Wall 2 |  | 6.09 | 2.4 |  | 21.6195 | sqm
| Wall 3 |  | 11.92 | 2.4 |  | 25.7472 | sqm
| Wall 4 |  | 6.09 | 2.4 |  | 21.6195 | sqm
Isolation Ward (A32,33,34)
| Wall 1 |  | 8.59 | 2.4 |  | 18.5544 | sqm
| Wall 2 |  | 2.92 | 2.4 |  | 2.9492 | sqm
| Wall 3 |  | 8.59 | 2.4 |  | 18.5544 | sqm
| Wall 4 |  | 1.04 | 2.4 |  | 1.0504 | sqm
Staff Ward (A37)
| Wall 1 |  | 2.64 | 2.4 |  | 5.7024 | sqm
| Wall 2 |  | 3.84 | 2.4 |  | 13.632 | sqm
| Wall 3 |  | 2.64 | 2.4 |  | 9.372 | sqm
| Wall 4 |  | 3.84 | 2.4 |  | 13.632 | sqm
Female Isolation Ward (A26,27,28)
| Wall 1 |  | 7.51 | 2.4 |  | 2.4032 | sqm
| Wall 2 |  | 2.96 | 2.4 |  | 2.9896 | sqm
| Wall 3 |  | 7.51 | 2.4 |  | 16.2216 | sqm
| Wall 4 |  | 2.96 | 2.4 |  | 2.9896 | sqm
Female Staff Ward (A23)
| Wall 1 |  | 2.71 | 2.4 |  | 5.8536 | sqm
| Wall 2 |  | 4.14 | 2.4 |  | 14.697 | sqm
| Wall 3 |  | 2.71 | 2.4 |  | 5.8536 | sqm
| Wall 4 |  | 4.14 | 2.4 |  | 14.697 | sqm
| Toilet (A18) |  | 1.005 | 2.01 |  | 2.02 | sqm
| Toilet (A25) |  | 2.76 | 2.96 |  | 8.1696 | sqm
| Toilet (A28.1) |  | 1.28 | 2.92 |  | 3.7376 | sqm
| Toilet (A35) |  | 2.75 | 2.65 |  | 7.2875 | sqm
| Toilet (A38) |  | 1.16 | 2.99 |  | 3.4684 | sqm
| Toilet (B9) |  | 1.47 | 2.51 |  | 3.6897 | sqm
| Toilet (A7.1) |  | 1.5 | 3.1 |  | 4.65 | sqm
| Toilet (A23.1) |  | 3 | 1.7 |  | 5.1 | sqm
| Toilet (A30.1) |  | 2.52 | 1.58 |  | 3.9816 | sqm
sqm
| Bath (A32.1) |  | 1.5 | 1.32 |  | 1.98 | sqm
| Bath (A32.2) |  | 1.5 | 1 |  | 1.5 | sqm
| Bath (24.1) |  | 1.835 | 1.5 |  | 2.7525 | sqm
For Wall
Toilet (A18)
| Wall 1 |  | 1.005 | 2.3 |  | 2.3115 | sqm
| Wall 2 |  | 2.01 | 2.3 |  | 4.623 | sqm
| Wall 3 |  | 1.005 | 2.3 |  | 2.3115 | sqm
| Wall 4 |  | 2.01 | 2.3 |  | 4.623 | sqm
Toilet (A25)
| Wall 1 |  | 2.96 | 2.3 |  | 6.808 | sqm
| Wall 2 |  | 2.76 | 2.3 |  | 6.348 | sqm
| Wall 3 |  | 2.96 | 2.3 |  | 6.808 | sqm
| Wall 4 |  | 2.76 | 2.3 |  | 6.348 | sqm
Toilet (A28.1)
| Wall 1 |  | 1.28 | 2.3 |  | 2.944 | sqm
| Wall 2 |  | 2.92 | 2.3 |  | 6.716 | sqm
| Wall 3 |  | 1.28 | 1.5 |  | 1.92 | sqm
| Wall 4 |  | 2.92 | 2.3 |  | 6.716 | sqm
Toilet (A35)
| Wall 1 |  | 2.75 | 2.3 |  | 6.325 | sqm
| Wall 2 |  | 2.65 | 2.3 |  | 6.095 | sqm
| Wall 3 |  | 2.75 | 2.3 |  | 6.325 | sqm
| Wall 4 |  | 2.65 | 2.3 |  | 6.095 | sqm
Toilet (A38)
| Wall 1 |  | 1.16 | 2.3 |  | 2.668 | sqm
| Wall 2 |  | 2.99 | 2.3 |  | 6.877 | sqm
| Wall 3 |  | 1.16 | 2.3 |  | 2.668 | sqm
| Wall 4 |  | 2.99 | 2.3 |  | 6.877 | sqm
Toilet (B9)
| Wall 1 |  | 1.47 | 2.3 |  | 3.381 | sqm
| Wall 2 |  | 2.51 | 2.3 |  | 5.773 | sqm
| Wall 3 |  | 1.47 | 2.3 |  | 3.381 | sqm
| Wall 4 |  | 2.51 | 2.3 |  | 5.773 | sqm
Toilet (A7.1)
| Wall 1 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 2 |  | 3.1 | 2.3 |  | 7.13 | sqm
| Wall 3 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 4 |  | 3.1 | 2.3 |  | 7.13 | sqm
Toilet (A23.1)
| Wall 1 |  | 3 | 2.3 |  | 6.9 | sqm
| Wall 2 |  | 1.84 | 2.3 |  | 4.232 | sqm
| Wall 3 |  | 3 | 2.3 |  | 6.9 | sqm
| Wall 4 |  | 1.84 | 2.3 |  | 4.232 | sqm
Toilet (A30.1)
| Wall 1 |  | 2.52 | 2.3 |  | 5.796 | sqm
| Wall 2 |  | 1.58 | 2.3 |  | 3.634 | sqm
| Wall 3 |  | 2.52 | 2.3 |  | 5.796 | sqm
| Wall 4 |  | 1.58 | 2.3 |  | 3.634 | sqm
Bath (A32.1)
| Wall 1 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 2 |  | 1.32 | 2.3 |  | 3.036 | sqm
| Wall 3 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 4 |  | 1.32 | 2.3 |  | 3.036 | sqm
Bath (A32.2)
| Wall 1 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 2 |  | 1 | 2.3 |  | 2.3 | sqm
| Wall 3 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 4 |  | 1 | 2.3 |  | 2.3 | sqm
Bath (24.1)
| Wall 1 |  | 1.835 | 2.3 |  | 4.2205 | sqm
| Wall 2 |  | 1.5 | 2.3 |  | 3.45 | sqm
| Wall 3 |  | 1.84 | 2.3 |  | 4.232 | sqm
| Wall 4 |  | 1.5 | 2.3 |  | 3.45 | sqm
RMO's Residence
| Toilet |  | 1.8 | 1.8 |  | 3.24 | sqm
| Bath |  | 1.8 | 2.6 |  | 4.68 | sqm
| Toilet |  | 1 | 2.9 |  | 2.9 | sqm
For Wall
| Toilet |  | 1.8 | 7.25 |  | 13.05 | sqm
| Bath |  | 1.8 | 8.96 |  | 16.128 | sqm
| Toilet |  | 1.8 | 8.3 |  | 14.94 | sqm
Nurse's Residence
| Toilet 1 |  | 2.5 | 1.5 |  | 3.75 | sqm
| Toilet 2 |  | 1.4 | 2.7 |  | 3.78 | sqm
For Wall
| Toilet 1 |  | 1.8 | 8.06 |  | 14.508 | sqm
| Toilet 2 |  | 1.8 | 8.47 |  | 15.246 | sqm
| Total a |  |  |  |  | 705.6625 | sqm
Deduction
Boys Ward (A30)
| Door 1 | 3 | 1.44 | 2.4 |  | 10.368 | sqm
| Door 2 | 1 | 1.37 | 2.4 |  | 3.288 | sqm
| Door 3 | 2 | 1.56 | 2.4 |  | 7.488 | sqm
| Door 4 | 1 | 1.275 | 2.4 |  | 3.06 | sqm
| Door 5 | 1 | 0.8 | 2.4 |  | 1.92 | sqm
Girls Ward (A22)
| Door 1 | 2 | 1.44 | 2.4 |  | 6.912 | sqm
| Door 2 | 1 | 1.54 | 2.4 |  | 3.696 | sqm
| Door 3 | 1 | 1.34 | 2.4 |  | 3.216 | sqm
| Door 4 | 1 | 1.21 | 2.4 |  | 2.904 | sqm
| Door 5 | 1 | 0.83 | 2.4 |  | 1.992 | sqm
| Door 6 | 1 | 1.25 | 2.4 |  | 3 | sqm
Isolation Ward (A32,33,34)
| Door 1 | 1 | 0.76 | 2.1 |  | 1.596 | sqm
| Door 2 | 2 | 1.19 | 2.4 |  | 5.712 | sqm
| Door 3 | 1 | 1.875 | 2.28 |  | 4.275 | sqm
| Window 1 | 1 | 0.66 | 0.6 |  | 0.396 | sqm
| Window 2 | 1 | 1.19 | 1.38 |  | 1.6422 | sqm
Staff Ward (A37)
| Door 1 | 1 | 1.22 | 2.4 |  | 2.928 | sqm
| Window 1 | 1 | 1.2 | 1.5 |  | 1.8 | sqm
| Window 2 | 1 | 1.09 | 1.5 |  | 1.635 | sqm
Female Isolation Ward (A26,27,28)
| Door 1 | 1 | 1.84 | 2.4 |  | 4.416 | sqm
| Door 2 | 1 | 1.18 | 2.4 |  | 2.832 | sqm
| Door 3 | 1 | 0.85 | 2.1 |  | 1.785 | sqm
| Window 1 | 2 | 1.15 | 1.4 |  | 3.22 | sqm
Female Staff Ward (A23)
| Door 1 | 1 | 1.34 | 2.4 |  | 3.216 | sqm
| Door 2 | 1 | 1.38 | 2.4 |  | 3.312 | sqm
| Window 1 | 1 | 1.94 | 1.5 |  | 2.91 | sqm
Toilet (A18)
| Door 1 | 1 | 0.78 | 2.1 |  | 1.638 | sqm
Toilet (A25)
| Door 1 | 1 | 0.68 | 1.89 |  | 1.2852 | sqm
| Window 1 | 1 | 1.09 | 0.89 |  | 0.9701 | sqm
Toilet (A28.1)
| Door 1 | 1 | 0.85 | 2.1 |  | 1.785 | sqm
| Window 1 | 1 | 1.28 | 1.18 |  | 1.5104 | sqm
Toilet (A35)
| Door 1 | 1 | 0.82 | 2.1 |  | 1.722 | sqm
| Window 1 | 1 | 1.06 | 1.18 |  | 1.2508 | sqm
Toilet (A38)
| Door 1 | 1 | 0.81 | 2.4 |  | 1.944 | sqm
Toilet (B9)
| Door 1 | 1 | 0.895 | 2.1 |  | 1.8795 | sqm
Toilet (A7.1)
| Door 1 | 1 | 1.51 | 2.1 |  | 3.171 | sqm
Toilet (A23.1)
| Door 1 | 1 | 0.85 | 2.1 |  | 1.785 | sqm
| Window 1 | 1 | 0.9 | 1.18 |  | 1.062 | sqm
Bath (34)
| Door 1 | 1 | 0.85 | 2.1 |  | 1.785 | sqm
| Window 1 | 1 | 0.67 | 0.6 |  | 0.402 | sqm
Bath (33)
| Door 1 | 1 | 0.85 | 2.1 |  | 1.785 | sqm
| Window 1 | 1 | 0.67 | 0.6 |  | 0.402 | sqm
Bath (24.1)
| Door 1 | 1 | 0.84 | 2.4 |  | 2.016 | sqm
RMO's Residence
Toilet
| Door | 1 | 2.1 | 0.82 |  | 1.722 | sqm
| Window | 1 | 0.6 | 1.1 |  | 0.66 | sqm
Bath
| Door | 1 | 2.1 | 1.07 |  | 2.247 | sqm
| Window | 1 | 0.6 | 1.07 |  | 0.642 | sqm
Toilet
| Door | 1 | 2 | 0.8 |  | 1.6 | sqm
Nurse's Residence
Toilet 1
| Door | 1 | 2.1 | 0.76 |  | 1.596 | sqm
| Window | 1 | 0.6 | 0.76 |  | 0.456 | sqm
Toilet 2
| Door | 1 | 2.1 | 0.95 |  | 1.995 | sqm
| Window 1 | 1 | 0.6 | 0.62 |  | 0.372 | sqm
| Window 2 | 1 | 0.6 | 0.79 |  | 0.474 | sqm
| Total b |  |  |  |  | 127.6762 | sqm
| Total (a-b) |  |  |  |  | 577.9863 | sqm
| At different location as per structure demand |  |  |  |  | 22.01 | sqm
| Total |  |  |  |  | 599.9963 | sqm
B9 | Providing & Fixing double skin full height 12 mm thick solid partition of make STYLAM or similar (upto the 7 feet), vertical members to be fixed on the SS plate and caping on the floor. Approved BWR ply as per IS:303, finished both side with approved 1 mm laminate surface complete with door shutter with laminate finish matching to the other available side of the partition, to be incorporated with necessary hinges, sliding bolt from inside, handle and all complete as per design, direction and approval of the Engineer.
| Total quantity |  |  |  |  | 30 | sqm
B10 | Providing wood work in frames of doors, windows, clerestory windows and other frames, wrought framed and fixed in position with hold fast lugs or with dash fasteners of required dia & length (hold fast lugs or dash fastener shall be paid for separately). Sal wood
| At different location as per structure demand |  |  |  |  | 1 | cum
B11 | Providing and fixing panelled or panelled and glazed shutters for doors, windows and clerestory windows, fixing with butt hinges of required size with necessary screws, excluding panelling which will be paid for separately, all complete as per direction of Engineer-in-charge. (Note: Butt hinges and necessary screws shall be paid separately) Second class teak wood
| At different location as per structure demand |  |  |  |  | 100 | sqm
B12 | Providing and fixing panelling or panelling and glazing in panelled or panelled and glazed shutters for doors, windows and clerestory windows (Area of opening for panel inserts excluding portion inside grooves or rebates to be measured). Panelling for panelled or panelled and glazed shutters 25 mm to 40 mm thick.
a | Second class teak wood |  |  |  |  | 100 | sqm
b | Float glass panes-4 mm thick glass pane (weight not less than 10 kg/sqm). |  |  |  |  | 40 | sqm
B13 | Steel work in built up tubular (round, square or rectangular hollow tubes etc.) trusses etc., including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer, including welding and bolted with special shaped washers etc. complete. Hot finished seamless type tubes
Garage
| 40X40X3MM | 16 | 3.47 |  | 3.45 | 191.544 | kg
For Canopy
| 200x200x4MM | 36 | 0.12 |  | 25.27 | 109.1664 | kg
| Steel Plate(3mm thick) | 144 | 0.15 | 0.09 | 23.55 | 45.7812 | kg
| 100x100x3MM | 36 | 1.86 |  | 9.1 | 16.926 | kg
| At different location as per structure demand |  |  |  |  | 136.58 | kg
| Total |  |  |  |  | 499.9976 | kg
B13 | Careful repair and refurbishment of existing wooden doors and windows, including minor dismantling, replacement of decayed wood with matching timber, tightening of joints, surface preparation, anti-termite treatment, repair/refixing of fittings, and replacement of broken or damaged glass panes where required, complete with polishing/painting as per engineer in charge.
C. Roofing works
C1 | Provide and fixing 19 mm thick marine plywood (water-resistant) onto rafters using suitable screws and washers, including all required fixing materials (nails, screws, washers, adhesives), aligning, leveling, cutting to fit at joints, and finishing. Work to be done complete, as per Engineer‑in‑Charge approval.
| Hospital total quantity |  |  |  |  | 1100 | sqm
C2 | Providng and fixing insulated PUFF sheet Roofing with the following specificifications -Panel Specifications: Roof shall be made of sandwich panel, made out of 0.50mm colour coated galvalume steel sheets spec 150gsm & 550mpa as as outer & inner cladding will be 0.40 mm colour coated galvalume sheet sheet spec 150 gsm & 550 mpa on both side of PUFF. Make of the sheet to be OEM TATA/JSW PRIME material. . The total thickness of panel will be 50/80 mm for roof, panel PU foam will be CFC free , self-extinguishing, Fire resistance type having density of 40 kg/cum. The Panel are joined together by tongue & groove method, complete in all respect including all the accessories. Fixing Mechanism: The sheeting will be fixed using galvanized self-drilling, self-tapping fasteners with EPDM seals to ensure secure attachment and weatherproofing.
| Hospital total quantity |  |  |  |  | 1100 | sqm
C3 | Providing and fixing flashings, Cappings, valleys manufactured same material as mentioned for roof sheets above in standard lengths of 2.5 mtr. And fixed by means of hex-head self-drilling stitching screws. 501 to 1000 mm Girth in Ridges, flashings, aprons, barge boards (Make of the sheet to be OEM TATA/JSW PRIME material)
| Hospital total quantity |  |  |  |  | 800 | metre
C4 | Providing and Fixing Gutters manufactured same material as mentioned for roof sheets without PUFF insultation above in standard lengths of 2.5 mtr. And fixed by means of hex-head self-drilling stitching screws. 501 to 1000 mm Girth (Make of the sheet to be OEM TATA/JSW PRIME material)
| 1 | 2 | 12.06 |  |  | 24.12 | rmt
| 2 | 1 | 23.96 |  |  | 23.96 | rmt
| 3 | 1 | 56.31 |  |  | 56.31 | rmt
| 4 | 2 | 21.41 |  |  | 42.82 | rmt
| 5 | 2 | 2.75 |  |  | 5.5 | rmt
| 6 | 1 | 9.07 |  |  | 9.07 | rmt
| 7 | 2 | 11.38 |  |  | 22.76 | rmt
| 8 | 2 | 4.89 |  |  | 9.78 | rmt
| 9 | 1 | 5.13 |  |  | 5.13 | rmt
| 10 | 1 | 9.47 |  |  | 9.47 | rmt
| 11 | 1 | 9.46 |  |  | 9.46 | rmt
| 12 | 1 | 184.7363 |  |  | 184.7363 | rmt
| At different location as per structure demand |  |  |  |  | 36.88 | rmt
| Total |  |  |  |  | 439.9963 | rmt
C5 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer onboth side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required.
| Garage |  |  |  |  | 29.45 | sqm
For Canopy
| Area 1 |  |  |  |  | 29.38 | sqm
| Area 2 |  |  |  |  | 32.06 | sqm
| Area 3 |  |  |  |  | 33.73 | sqm
| At different location as per structure demand |  |  |  |  | 15.38 | sqm
| Total |  |  |  |  | 140 | sqm
C6 | Providing and fixing precoated galvanised steel sheet roofing accessories of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05 mm) with Zinc coating 120 gram per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete : Flashings/ Aprons.( Upto 600 mm)
| Garage |  |  |  |  | 29.45 | sqm
For Canopy
| Area 1 |  |  |  |  | 29.38 | sqm
| Area 2 |  |  |  |  | 32.06 | sqm
| Area 3 |  |  |  |  | 33.73 | sqm
| At different location as per structure demand |  |  |  |  | 15.38 | sqm
| Total |  |  |  |  | 140 | sqm
C7 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete.
For Garage
| 50 X 50 X 3MM | 3 | 5.74 |  | 4.4 | 75.768 | kg
|  | 6 | 6.029 |  | 4.4 | 159.1656 | kg
For Canopy
| 50 X 50 X 3MM | 75 | 1.385 |  | 4.4 | 457.05 | kg
| At different location as per structure demand |  |  |  |  | 38.02 | kg
| Total |  |  |  |  | 730.0036 | kg
D. Plumbing & Sanitary works
D1 | Providing and fixing white vitreous china extended wall mounting water closet of size 780x370x690 mm of approved shape including providing & fixing white vitreous china cistern with dual flush fitting, of flushing capacity 3 litre/ 6 litre (adjustable to 4 litre/ 8 litres), including seat cover, and cistern fittings, nuts, bolts and gasket etc complete.
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 3 |  |  |  | 3 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 3 |  |  |  | 3 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 13 | nos
D2 | Providing and fixing wash basin with C.I. brackets, 15 mm C.P. brass pillar taps, 32 mm C.P. brass waste of standard pattern, including painting of fittings and brackets, cutting and making good the walls wherever require: White Vitreous China Flat back wash basin size 450x 300 mm with single 15 mm C.P. brass pillar tap
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 2 |  |  |  | 2 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 2 |  |  |  | 2 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 11 | nos
D3 | Providing and fixing CP Brass 32 mm size Bottle Trap of approved quality & make and as per the direction of Engineer-in-charge.
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 2 |  |  |  | 2 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 2 |  |  |  | 2 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 11 | nos
D4 | Providing and fixing toilet paper holder : C.P. brass
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 3 |  |  |  | 3 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 3 |  |  |  | 3 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 13 | nos
D5 | Providing and fixing Health faucet with 1 metre long Flexible tube and C.P. wall hook with PVC & SS Screws wherever required make and as per the direction of Engineer-in-charge.
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 3 |  |  |  | 3 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 3 |  |  |  | 3 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 13 | nos
D6 | Providing and fixing of C.P. Soap dish complete as per instruction of Engineer-in-charge.
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 1 |  |  |  | 1 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 1 |  |  |  | 1 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 9 | nos
D7 | Providing and fixing C.P Towel Rail 600mm long fixed to PVC cleats with C.p brass screws including cutting and making good the walls wherever required.
| Bath (A32.1) | 1 |  |  |  | 1 | nos
| Bath (A32.2) | 1 |  |  |  | 1 | nos
| Bath (24.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 3 | nos
D8 | Providing and fixing C.P Single lever concealed diverter and Bath spout for bath and shower with Button at Top complete as per direction of the Engineer-in-charge
| Bath (A32.1) | 1 |  |  |  | 1 | nos
| Bath (A32.2) | 1 |  |  |  | 1 | nos
| Bath (24.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 3 | nos
D9 | Providing and Fixing Shower Head Over head rose shower with revoling joint ( with boday roation) & 115 mm long shower arm complete as directed by enginner in charge
| Bath (A32.1) | 1 |  |  |  | 1 | nos
| Bath (A32.2) | 1 |  |  |  | 1 | nos
| Bath (24.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 3 | nos
D10 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.15 mm nominal bore
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 3 |  |  |  | 3 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 3 |  |  |  | 3 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 13 | nos
D11 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. 15 mm nominal bore
| Toilet (A18) | 2 |  |  |  | 2 | nos
| Toilet (A25) | 4 |  |  |  | 4 | nos
| Toilet (A28.1) | 2 |  |  |  | 2 | nos
| Toilet (A35) | 4 |  |  |  | 4 | nos
| Toilet (A38) | 2 |  |  |  | 2 | nos
| Toilet (B9) | 2 |  |  |  | 2 | nos
| Toilet (A7.1) | 2 |  |  |  | 2 | nos
| Toilet (A23.1) | 2 |  |  |  | 2 | nos
| Toilet (A30.1) | 2 |  |  |  | 2 | nos
| Total |  |  |  |  | 22 | nos
D12 | Providing and fixing C.P. brass angle valve for basin mixer and geyser points of approved quality conforming to IS:8931 15 mm nominal bore
| Toilet (A18) | 2 |  |  |  | 2 | nos
| Toilet (A25) | 4 |  |  |  | 4 | nos
| Toilet (A28.1) | 2 |  |  |  | 2 | nos
| Toilet (A35) | 4 |  |  |  | 4 | nos
| Toilet (A38) | 2 |  |  |  | 2 | nos
| Toilet (B9) | 2 |  |  |  | 2 | nos
| Toilet (A7.1) | 2 |  |  |  | 2 | nos
| Toilet (A23.1) | 2 |  |  |  | 2 | nos
| Toilet (A30.1) | 2 |  |  |  | 2 | nos
| Total |  |  |  |  | 22 | nos
D13 | Providing and fixing of C.P towel ring square/circular fixed to wooden cleats with C.P brass screws including cutting and making good the walls wherever required.
| Toilet (A18) | 1 |  |  |  | 1 | nos
| Toilet (A25) | 1 |  |  |  | 1 | nos
| Toilet (A28.1) | 1 |  |  |  | 1 | nos
| Toilet (A35) | 1 |  |  |  | 1 | nos
| Toilet (A38) | 1 |  |  |  | 1 | nos
| Toilet (B9) | 1 |  |  |  | 1 | nos
| Toilet (A7.1) | 1 |  |  |  | 1 | nos
| Toilet (A23.1) | 1 |  |  |  | 1 | nos
| Toilet (A30.1) | 1 |  |  |  | 1 | nos
| Total |  |  |  |  | 9 | nos
D14 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings and fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per direction of Engineer in Charge. Concealed work, including cutting chases and making good the walls etc.
| 15 mm nominal dia Pipes |  |  |  |  | 100 | metre
| 20 mm nominal dia Pipes |  |  |  |  | 80 | metre
| 25 mm nominal dia Pipes |  |  |  |  | 80 | metre
| 32 mm nominal dia Pipes |  |  |  |  | 70 | metre
D15 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per direction of Engineer in Charge. External work
| 15 mm nominal dia Pipes |  |  |  |  | 150 | metre
| 20 mm nominal dia Pipes |  |  |  |  | 120 | metre
| 25 mm nominal dia Pipes |  |  |  |  | 60 | metre
| 32 mm nominal dia Pipes |  |  |  |  | 50 | metre
D16 | Providing and laying Non Pressure NP-3 class (Medium duty) R.C.C. pipes including collars/spigot jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of jointsetc. Complete 450 mm dia RCC pipes.
| For drains |  |  |  |  | 20 | rmt
D17 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement : 4 coarse sand ) with R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 coarse sand (zone-III) : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand (zone-III) : 8 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5
| For drain and plinth protection |  |  |  |  | 2 | each
#REF!
E1 | Supply, Wiring, Testing & Commissioning for switch board controlled light points with 3 X 1.5sq.mm FRLS PVC insulated copper wire and earthing with 1.5 sq.mm. FRLS PVC insulated copper wire in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of modular switches as specified complete with modular plate with GI boxes of suitable as complete as required.
E1.1 | First Point (One point controlled by one no. 6 amps switch.) (Normal Light Point)
| Hospital |  |  |  |  | 115 | nos.
| RMO's Residence |  |  |  |  | 24 | nos.
| Nurse's residence |  |  |  |  | 17 | nos.
| Total |  |  |  |  | 156 | Nos
E1.2 | same as the above for Looping Point
| Hospital |  |  |  |  | 24 | nos.
| RMO's Residence |  |  |  |  | 0 | nos.
| Nurse's residence |  |  |  |  | 0 | nos.
| Total |  |  |  |  | 24 | Nos
E2 | Supply, Wiring, Testing & Commissioning for MCB controlled light points with 2 x 2.5 + 1 X 1.5 sq.mm FRLS PVC insulated copper wires in recessed / surface mounted in in insurface / recessed Medium class FRLS PVC conduit, surface tee, saddles, conduit fixing material, MS Connector, along with all required fittings. (Cost of MCB not to be included)
E2.1 | First Point (First light points controlled by one no.6A SP MCB)
| Hospital |  |  |  |  | 30 | nos.
| RMO's Residence |  |  |  |  | 6 | nos.
| Nurse's residence |  |  |  |  | 4 | nos.
| Total |  |  |  |  | 40 | Nos
E2.2 | same as above for the Looping Point
| Hospital |  |  |  |  | 7 | nos.
| RMO's Residence |  |  |  |  | 0 | nos.
| Nurse's residence |  |  |  |  | 0 | nos.
| Total |  |  |  |  | 7 | Nos
E3 | Supply, Wiring, Testing & Commissioning for 6 A multistandard shutterd switched socket outlet with 3 x 1.5 sq mm FRLS PVC insulated copper wire & earthing with 1.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, surface tee, saddles,conduit fixing material, MS Connector, including providing & fixing of 6amps modular switch, socket complete with modular plate with suitable size of GI box complete in all respect.
| Hospital |  |  |  |  | 67 | nos.
| RMO's Residence |  |  |  |  | 12 | nos.
| Nurse's residence |  |  |  |  | 11 | nos.
| Total |  |  |  |  | 90 | Nos
E4 | Supply, Wiring, Testing & Commissioning for 1 nos, 16 A shuttered, switched socket outlets with 2 x4 +1 x 2.5 sq.mm FRLS PVC insulated copper wire & earthing with 2.5 sq.mm FRLS PVC insulated copper wire in surface / recessed Medium class FRLS PVC conduit, including providing & fixing of 1 nos. of 16amps modular switched socket outlets alongwith 1nos 16 A switch with modular plate with GI box complete.
| Hospital |  |  |  |  | 43 | nos.
| RMO's Residence |  |  |  |  | 7 | nos.
| Nurse's residence |  |  |  |  | 4 | nos.
| Total |  |  |  |  | 54 | Nos
E5 | Wiring for projector/Geyser points with 2 x 4 + 1 x 2.5 sq mm FRLS PVC insulated strande·d copper con-ductor wires in concealed FRLS PVC conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switch near the white board and 16 amps 5 pin socket near the projector in ceiling , 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) ( 1 point per circuits)
| Hospital |  |  |  |  | 6 | nos.
| RMO's Residence |  |  |  |  | 1 | nos.
| Nurse's residence |  |  |  |  | 2 | nos.
| Total |  |  |  |  | 9 | Nos
E6 | Wiring for A/C outlet points with 2X4.0+1X2.5 sq mm FRLS PVC insulated stranded copper conductor wires in FRLS PVC conduit/wall/floor ducts as directed including 25 A single phase Triny type socket with 25 A SP MCB (motor duty), 2 mm thick providing and Nos. fixing M.S. box to house the above duly painted and earthing with 2.5 sq. mm FRLS PVC insulated stranded Copper Conductor wires complete as required.
| Hospital |  |  |  |  | 6 | nos.
| RMO's Residence |  |  |  |  | 2 | nos.
| Nurse's residence |  |  |  |  | 2 | nos.
| Total |  |  |  |  | 10 | Nos
E7 | Supply and wiring of exhaust fan point with 3 X 1.5 sq.mm FRLS PVC insulated copper conductor cable in in surface / recessed GI conduit, fixing on surface or wall/ceiling including fixing of saddles etc. including galvanised M.S. box, modular range of plate switches, 6A socket, modular cover plate, PVC insulated copper earth wire etc. complete as required.
| Hospital |  |  |  |  | 11 | nos.
| RMO's Residence |  |  |  |  | 3 | nos.
| Nurse's residence |  |  |  |  | 3 | nos.
| Total |  |  |  |  | 17 | Nos
E8 | Wiring for the Ceiling fan points with 3X1.5 Sq.mm PVC insulated stranded copper conductor wires in concealed FRLS PVC. conduits in ceiling / walls as directed including providing Hexagonal fan Box , Electronic fan regulator,6 amp switch, 5 sided G.I. Boxes for housing the regulator and earthing complete as required.
| Hospital |  |  |  |  | 32 | nos.
| RMO's Residence |  |  |  |  | 5 | nos.
| Nurse's residence |  |  |  |  | 4 | nos.
| Total |  |  |  |  | 41 | Nos
E9.1 | 20 mm dia conduit ( 1.6 mm thick) |  |  |  |  | 150 | metre
E9.2 | 25 mm dia conduit (1.6 mm thick) |  |  |  |  | 80 | metre
E9.3 | 32 mm dia conduit (2.0 mm thick) |  |  |  |  | 65 | metre
E10 | Supply,installing ,connecting testing and commissioning of the following double door 1/4 rows vertical type 1.6 mm thick and 1. 4 thick door sheet steel enclosed fully recessed type, TPN Miniature Circuit Breakers Distribution Boards dust proof, verm-in proof, with hinged and lockable doors complete with DP MCB's and inter- connection with copper wire , insulated copper bus bar , cable glands-/conduit entry bushes, bonding to earth and paint-ing. Also provide separate neutral: busbar for each phase. Provide separate ,Earth Links for each phase. Use brass thimbles for connections of all: wires. 1 row for single phase and 4 rows for 3 phase. Provide separate 4 way 63 A main neutral link also. The phase busbar links shall be factory pre insulated.
E10.1 | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB.
| Total quantity |  |  |  |  | 5 | nos
E10.2 | 8 Way TPN DB, each phase consisting of 6 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB.
| Total quantity |  |  |  |  | 4 | nos
E10.3 | 14 Way TPN DB, each phase consisting of 12 Nos. 10/20 AMP SP MCB's and controlled by one number 100 mA sensitivity 63 AMPS DP ELCB backed up with 1 no 63 Amps 4 pole MCB.
| Total quantity |  |  |  |  | 4 | nos
E11 | Supply & Installation, Testing & Commissioning of 250 mm dia exhaust fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ).
| Hospital |  |  |  |  | 11 | nos.
| RMO's Residence |  |  |  |  | 3 | nos.
| Nurse's residence |  |  |  |  | 3 | nos.
| Total |  |  |  |  | 17 | Nos
E12 | Supply, Installation, Testing & Commissioning of 1200 mm dia 5 Star rated ceiling fan with all accessories as complete as required. (Make -Havells / Oriant / Bajaj ).
| Hospital |  |  |  |  | 32 | nos.
| RMO's Residence |  |  |  |  | 5 | nos.
| Nurse's residence |  |  |  |  | 4 | nos.
| Total |  |  |  |  | 41 | Nos
E13 | Supplying of light fixtures as per sample approved.