## Sheet1
BOQ FOR RAIN WATER TANK
S.No. | Description of Item | Unit | Quantity | Rate | Amount
1 | Providing and inserting 12mm dia galvanised steel injection nipple in honey comb area and along crack line including drilling of holes of required diametre (20mm to 30mm) up to depth from 30mm to 80mm at 1 meter c/c and making the hole & crack dust free by blowing compressed air, sealing the distance between injection nipple with adhesive chemical of approved make and allow it to cure complete as per direction of Engineer-In-Charge. | Each | 700
2 | Cleaning of base surface, cutting all construction joints in U/V shape upto 10 to 15mm.Providing and applying integral crystalline slurry of hydrophilic in nature for waterproofing treatment to the RCC structures like retaining walls of the basement, water tanks, roof slabs, podiums, reservior, sewage & water treatment plant, tunnels / subway and bridge deck etc., prepared by mixing in the ratio of 5 : 2 (5 parts integral crystalline slurry : 2 parts water) for vertical surfaces and 3 : 1 (3 parts integral crystalline slurry : 1 part water) for horizontal surfaces and applying the same from negative (internal) side with the help of synthetic fiber brush. The material shall meet the requirements as specified in ACI-212-3R-2010 i.e by reducing permeability of concrete by more than 90% compared with control concrete as per DIN 1048 and resistant to 16 bar hydrostatic pressure on negative side. The crystalline slurry shall be capable of self-healing of cracks up to a width of 0.50mm. The work shall be carried out all complete as per specification and the direction of the engineer-incharge.The product performance shall carry guarantee for 10 years against any leakage. For vertical surface two coats @ 0.70 kg per sqm For horizontal surface one coat @1.10 kg per sqm. | Sqm | 350
3 | Cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement. 20 mm cement plaster | Sqm | 500
4 | Electrical BOQ
a. | Supplying of four core,4x25 sqmm one number aluminium conductor PVC insulated and PVC sheathed armoured power cable 110 voltage grade directed in ground below one meter depth from Virgin Villa FP to till site ( as per HPPWD specifications) Make : HAVELLS and equivelant | RM | 105
b. | S&L 8 SWG GI wire cables | RM | 210
c. | S&F 100 Amps Four pole MCCB with encloser Make L&T and equivelant | Each | 1
d. | fixing Pump 10 HP, 3 Phase, Electrical Driven (for lifting of water) Make : Kirlosker/ Cromptom/ Greeves (all neccsary fitting in the scope of contractor pump provided by school) | Each | 1
e. | S&F DOL starter suitable capacity for10 HP pump Make: L&T and equivelant | Each | 1
g | fixing 50mm GI pipe medium grade icluding all accessories incl neceesary excavation/ road cutting Make : Jindal and equivelant (fittting in the scope of contractor pipe will be provided by school ) | RM | 10
h | S&F 50mm dia Gun Metal gate valve | Each | 1
i | connection of 6 inches pvc tank with core cutting and all neccsary fitting | job | 1
5 | Provision of water proof shed for fixing of pump, starter and MCCB of size 1.80 Mtr x1.30 Mtrx 1.5 Mtr (ht) with CGI sheet roofing in heritage finish complete with following specifications :- ( a) Surface excavation and removal of soil (b). 50mm PCC flooring over100mm thick hardcore with 150mm raised platform for fixing pump (c). Brick wall in CM 1:6, 1.20 Mtr high one side for fixing of Starter MCCB box (d) MS framework and CGI Sheeting on roof and three sides with door shutter and locking arragement (e) Plastering to brick wall and applying three coats of Cement based paint over a coat of primer (f) Applying two coats of synthetic enamel paint over a coat of red oxide zinc chrome primer complete. | Job | 1
6 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth out side the site as per government/authority norms without stacking and lift up to 6m (includes dressing of bottom, side strutting,timbering,shoring,trimming of sides, dewatering etc. Surface preparation as per specs to receive PCC. Plan area of foundation as per drawing is payable. The cost of excavation required for working space, supporting side shuttering of retaining walls, foundation, slope required for stability of soil etc are deemed to be included in the rates. Excess excavation done should be made good by contractor free of cost as per direction of engineer in charge) Quote the item keeping in mind to compensate with amount of earth excavated as it become property of contractor.(Contractor should visit the site to know the location of excavation and shall quote keeping in mind the items required to dismantle to execute the excavation which should be included in the cost) 2.6.1 All kinds of soil
| a. lead upto 50 m. | Cum | 5
7 | Providing and laying in position machine mixed plain cement concrete of specified grade including ramming, consolidating, leveling and curing, also the cost of centering and shuttering 1:3:6 (1 Cement : 3 coarse sand (zone-III) : 6 graded stone aggregate 20 mm nominal size) | Cum | 5
8 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor etc., up to floor five level, excluding the cost of centering, shuttering and finishing:
| 1:3:6 (1 cement : 3 coarse sand (zone-III) : 6 graded stone aggregate 20 mm nominal size) | Cum | 1
9 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level (M25) CEMENT - ULTRATECH ,ACC,AMBUJA | Cum | 2
10 | Supply and back filling of new earth work(excluding rock) in trenches, plinth, sides of foundation etc. in layers not exceeding 20cm in depth consolidating each deposited layer by ramming (by Mechanical compactor )and watering, within the battery limits. (Backfilling shall be paid up to the vertical outer edge of lean concrete and retaining wall only) -All kinds of soil | Cum | 5
11 | Providing & fixing in position reinforcement of various diameters for R.C.C. pile caps, footings, foundations, slabs, beams & columns, canopies, staircases, newels, chajjas, lintels, pardies, copings, fins, arches, etc… as per detailed design & drawing & schedules including cutting, bending, hook in the bars, binding the wires (18G black annealed) double fold or tack welding and supporting as requires completed. a) TMT - Sail .tata
| A. For all works upto plinth level | Kgs. | 100
12 | Shuttering
a | Providing and removing steel centering,plywood/steel formwork,shuttering, popping etc. and removal of form work for foundation ,footings,bases of columns for mass concrete including cost of all materials, labour complete as per specification. | Sqm | 5
Following are the terms and conditions:-
1 | The actual quantity will be measured as per site and will be paid accordingly.
2 | The quantities of work can be increased or decreased without assigning any reason.
3 | Security @5% shall be deducted from the bill & and will be released after Twelve Months.
4 | Penalty @2% of the total bill shall be imposed for each week of delay of work.
5 | 5% of the total bill shall be imposed as penalty in case the work is not finished and contractor leaves the work.
6 | The rates quoted by the contractor shall be inclusive of all taxes and charges,nothing extra will be paid for any kind of other taxes.
7 | The rates quoted by the contractor shall be inclusive of all taxes and charges,nothing extra will be paid for any kind of other taxes.
8 | The School can terminate this agreement without giving any notice
9 | The Contractor will bear and be responsible for all statutory liabilities such as PF, ESI etc as applicable.
10 | The Contractor will take all safety measures and you will be responsible for any accident /incident and other liabilities related to accident /incident.
11 | In case of any difference and dispute the Arbitrator decision will be final. The Arbitrator will be nominated by Headmaster, In case the matter is not amicably settled, the court at Solan alone shall have be Jurisdiction to decide the same.
12 | Scafflofing charges is inlcuded in the quoted rates.
13 | Electricity will be provided at one point to contractor via a sub meter installed and will be charged accordingly.
14 | Water will be in the scope of contractor own arrangement basis.
15 | Approved make of waterproofing material - Dr.fixit and SIKA
16 | The product performance shall carry guarantee for 10 years against any leakage .The contractor would be responsible for ensuring that the waterproofing work meets the standards specified in the contract and that it will remain effective for the duration of the warranty period. If there are any issues with the waterproofing during the warranty period, the contractor would be required to repair it at no cost to the client.
17 | The contractor is responsible for providing and managing all the necessary materials, including civil materials, scaffolding, and any other job-related materials required for the waterproofing work.